## OPTIMA Compact
QUICK - CALC OPTIMA Compact & OPTIMA Compact Veriflow
Setting & Selection program
Input
Input Q = | 1000 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp(kPa) | Pre-set | Min. ∆P (kPa)
DN10 Low 2,5 | 30-200 | 14-800 | NOT POSSIBLE | NOT POSSIBLE
DN10 Low 5,0 | 65-370 | 14-800 | NOT POSSIBLE | NOT POSSIBLE
DN15 Low 2,5 | 30-200 | 14-800 | NOT POSSIBLE | NOT POSSIBLE
DN15 Low 5,0 | 65-370 | 14-800 | NOT POSSIBLE | NOT POSSIBLE
DN15 High 2,5 | 100-575 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN15 High 5,0 | 220-1330 | 16-800 | 3.0261 | 20.682
DN15 High 5,5 | 300-1800 | 18-800 | 2.4 | 24.1914
DN20 High 2,5 | 100-575 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN20 High 4,0 * | 160-990 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN20 High 5,0 | 220-1330 | 16-800 | 3.0261 | 20.682
DN20 High 5,5 | 300-1800 | 18-800 | 2.4 | 24.1914
DN25 Low 5,5 | 280-1800 | 15-800 | 2.5 | 20.2197
DN25L High 5,5 | 600-3609 | 17-800 | 1.052 | 17.4491
DN32 | 550-4001 | 18-800 | 1.0431 | 18.1599
DN40 | 1370-9500 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
DN50 | 1400-11500 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
*) Not standard product
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
Type | Min | Max | Evaluering af Flow
DN10 Low 2,5 | 30 | 200 | UDEN FOR OMRÅDET
DN10 Low 5,0 | 65 | 370 | UDEN FOR OMRÅDET
DN15 Low 2,5 | 30 | 200 | UDEN FOR OMRÅDET
DN15 Low 5,0 | 65 | 370 | UDEN FOR OMRÅDET
DN15 High 2,5 | 100 | 575 | UDEN FOR OMRÅDET
DN15 High 5,0 | 220 | 1330 | 1000
DN15 High 5,5 | 300 | 1800 | 1000
DN20 High 2,5 | 100 | 575 | UDEN FOR OMRÅDET
DN20 High 4,0 | 160 | 990 | UDEN FOR OMRÅDET
DN20 High 5,0 | 220 | 1330 | 1000
DN20 High 5,5 | 300 | 1800 | 1000
DN25 Low 5,5 | 280 | 1800 | 1000
DN25L High 5,5 | 600 | 3609 | 1000
DN32 | 550 | 4001 | 1000
DN40 | 1370 | 9500 | UDEN FOR OMRÅDET
DN50 | 1400 | 11500 | UDEN FOR OMRÅDET

## OPTIMA Compact Flanged
QUICK - CALC OPTIMA Compact & OPTIMA Compact Veriflow
Setting & Selection program
Input
Input Q = | 10.5 | (m3/h) Flow
Dimension & Type | Range |  | Calculation
| Flow (m3/h) | Range ∆Pp(kPa) | Pre-set | Min. ∆P (kPa)
DN50 Ultra High Flow | 1.40-11.5 | 10-800 | 3.8244 | 33.6931
DN50 Standard Low Flow | 2.50-15.0 | 7-800 | 3.0743 | 12.4383
DN50 Standard High Flow | 3.90-24.0 | 19-800 | 1.8612 | 20.3949
DN65 Ultra Low Flow | 3.00-16.0 | 10-800 | 2.8462 | 11.7117
DN65 Ultra High Flow | 4.20-24.0 | 19-800 | 1.839 | 19.7833
DN65 Standard Low Flow | 4.40-25.0 | 15-800 | 1.7931 | 17.5931
DN65 Standard High Flow | 6.00-35.0 | 30-800 | 1.1976 | 31.0776
DN80 Ultra Low Flow | 4.40-25.0 | 15-800 | 1.7946 | 17.3711
DN80 Ultra High Flow | 6.00-35.0 | 30-800 | 1.2023 | 27
DN80 Standard Low Flow | 5.30-34.0 | 16-800 | 1.3573 | 9
DN80 Standard High Flow | 7.00-43.0 | 23-800 | 0.94888 | 15
DN100 Ultra Low Flow | 5.30-34.0 | 16-800 | 1.3325 | 9
DN100 Ultra High Flow | 7.00-43.0 | 23-800 | 0.9458 | 15
DN100 Standard Low Flow | 12.1-68.0 | 20-800 | NOT POSSIBLE | NOT POSSIBLE
DN100 Standard High Flow | 14.8-90.0 | 30-800 | NOT POSSIBLE | NOT POSSIBLE
DN125 Ultra Low Flow | 12.1-68.0 | 20-800 | NOT POSSIBLE | NOT POSSIBLE
DN125 Ultra High Flow | 14.8-90.0 | 30-800 | NOT POSSIBLE | NOT POSSIBLE
DN125 Standard Low Flow | 18.5-110 | 16-800 | NOT POSSIBLE | NOT POSSIBLE
DN125 Standard High Flow | 23.0-135 | 27-800 | NOT POSSIBLE | NOT POSSIBLE
DN150 Standard Low Flow | 25.6-148 | 21-800 | NOT POSSIBLE | NOT POSSIBLE
DN150 Standard High Flow | 32.0-195 | 33-800 | NOT POSSIBLE | NOT POSSIBLE
DN200 Standard Low Flow | 95.0-210 | 11-800 | NOT POSSIBLE | NOT POSSIBLE
DN200 Standard High Flow | 130-280 | 31-800 | NOT POSSIBLE | NOT POSSIBLE
DN250 Standard Low Flow | 190-475 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
DN250 Standard High Flow | 245-600 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN300 Standard Low Flow | 190-475 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
DN300 Standard High Flow | 245-600 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
Type | Min | Max | Evaluering Flow
DN50 Ultra High Flow | 1.4 | 11.5 | 10.5
DN50 Standard Low Flow | 2.5 | 15 | 10.5
DN50 Standard High Flow | 3.9 | 24 | 10.5
DN65 Ultra Low Flow | 3 | 16 | 10.5
DN65 Ultra High Flow | 4.2 | 24 | 10.5
DN65 Standard Low Flow | 4.4 | 25 | 10.5
DN65 Standard High Flow | 6 | 35 | 10.5
DN80 Ultra Low Flow | 4.4 | 25 | 10.5
DN80 Ultra High Flow | 6 | 35 | 10.5
DN80 Standard Low Flow | 5.3 | 34 | 10.5
DN80 Standard High Flow | 7 | 43 | 10.5
DN100 Ultra Low Flow | 5.3 | 34 | 10.5
DN100 Ultra High Flow | 7 | 43 | 10.5
DN100 Standard Low Flow | 12.1 | 68 | UDEN FOR OMRÅDET
DN100 Standard High Flow | 14.8 | 90 | UDEN FOR OMRÅDET
DN125 Ultra Low Flow | 12.1 | 68 | UDEN FOR OMRÅDET
DN125 Ultra High Flow | 14.8 | 90 | UDEN FOR OMRÅDET
DN125 Standard Low Flow | 18.5 | 110 | UDEN FOR OMRÅDET
DN125 Standard High Flow | 23 | 135 | UDEN FOR OMRÅDET
DN150 Standard Low Flow | 25.6 | 148 | UDEN FOR OMRÅDET
DN150 Standard High Flow | 32 | 195 | UDEN FOR OMRÅDET
DN200 Standard Low Flow | 95 | 210 | UDEN FOR OMRÅDET
DN200 Standard High Flow | 130 | 280 | UDEN FOR OMRÅDET
DN250 Standard Low Flow | 190 | 475 | UDEN FOR OMRÅDET
DN250 Standard High Flow | 245 | 600 | UDEN FOR OMRÅDET
DN300 Standard Low Flow | 190 | 475 | UDEN FOR OMRÅDET
DN300 Standard High Flow | 245 | 600 | UDEN FOR OMRÅDET

## COMBIFLOW
QUICK - CALC COMBIFLOW 6-Way
Setting & Selection program
Input
Flow cooling | 30 | l/h
Flow heating | 830 | l/h
|  |  | Calculation Pre-set |  | Calculation minimum diff. Pressure |  | Calculation total pressure loss
Dimension | Range |  | Cooling | Heating | Cooling | Heating | Cooling | Heating
| Flow l/h | Range ∆Pp (kPa) | Pre-set scale | Pre-set scale | Min. ∆P (kPa) | Min. ∆P (kPa) | Total ∆P (kPa) | Total ∆P (kPa)
DN15 Low | 30 - 830 | 4 - 400 | 0.5 | 4 | 4 | 19 | 10 | 26
DN15 | 210 - 1200 | 15 - 400 | NOT POSSIBLE | 2.8 | NOT POSSIBLE | 18 | NOT POSSIBLE | 25
DN20 | 460 - 4250 | 17-400 | NOT POSSIBLE | 1.6 | NOT POSSIBLE | 18 | NOT POSSIBLE | 19
Bacnet Value = 1 x Preset Scale
Modbus Value = 10 x Preset scale
Analog Pre-set
Dimension | Cooling |  | Heating
| Voltage preset 0-10V | Current preset 4-20mA | Voltage preset 0-10V | Current preset 4-20mA
DN15 Low | 3.9 | 10.2 | 10 | 20
DN15 | NOT POSSIBLE | NOT POSSIBLE | 8.7 | 17.9
DN20 | NOT POSSIBLE | NOT POSSIBLE | 7.3 | 15.7
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
|  |  | Køling | Varme | Vinkel køling | Vinkel varme |  | Best Match
Type | Min | Max | Evaluering Flow | Evaluering Flow | -10 | -45 |  |  | DN15 Low | DN15 | DN20
DN15 Low | 30 | 830 | 30 | 830 | #VALUE! | -33 |  | Cooling | 30 | 210 | 460
DN15 | 210 | 1200 | UDEN FOR OMRÅDET | 30 | #VALUE! | -21 |  | Heating | 830 | 810 | 910
DN20 | 460 | 4250 | UDEN FOR OMRÅDET | 30
Flow |  |  | Preset | Minimum DP |  |  | Total pumpe DP
DN15 Low | DN15 | DN20 |  | DN15 Low | DN15 | DN20 | DN15 Low | DN15 | DN20
30 |  |  | 0.5 | 4 |  |  | 10
35 |  |  | 0.6 | 4 |  |  | 10
50 |  |  | 0.8 | 5 |  |  | 10
65 | 210 | 460 | 1 | 8 | 15 | 17 | 10 | 15 | 17
75 | 260 | 600 | 1.2 | 10 | 15 | 17 | 11 | 15 | 18
85 | 320 | 740 | 1.4 | 11 | 15 | 17 | 12 | 16 | 18
100 | 380 | 910 | 1.6 | 11 | 15 | 18 | 12 | 16 | 19
120 | 430 | 1110 | 1.8 | 12 | 15 | 18 | 13 | 17 | 19
140 | 490 | 1310 | 2 | 13 | 15 | 18 | 14 | 17 | 20
190 | 550 | 1540 | 2.2 | 14 | 16 | 19 | 15 | 19 | 22
240 | 610 | 1760 | 2.4 | 14 | 17 | 20 | 15 | 21 | 24
310 | 700 | 2020 | 2.6 | 14 | 17 | 21 | 15 | 23 | 26
380 | 810 | 2310 | 2.8 | 14 | 18 | 22 | 16 | 25 | 28
460 | 910 | 2600 | 3 | 15 | 19 | 23 | 18 | 27 | 30
560 | 1000 | 3000 | 3.2 | 15 | 20 | 26 | 19 | 29 | 35
660 | 1090 | 3400 | 3.4 | 16 | 21 | 29 | 21 | 31 | 40
730 | 1150 | 3730 | 3.6 | 17 | 21 | 32 | 23 | 32 | 46
780 | 1170 | 3990 | 3.8 | 18 | 22 | 35 | 25 | 34 | 51
830 | 1200 | 4250 | 4 | 19 | 23 | 38 | 26 | 36 | 56
|  |  | DN15 LOW |  |  |  | DN15 |  |  |  | DN20
Flow |  |  | Voltage |  | Current |  | Voltage |  | Current |  | Voltage |  | Current
DN15 Low | DN15 | DN20 | Heating | Cooling | Heating | Cooling | Heating | Cooling | Heating | Cooling | Heating | Cooling | Heating | Cooling
30 |  |  | 6.1 | 3.9 | 13.8 | 10.2
35 |  |  | 6.2 | 3.8 | 13.9 | 10.1
50 |  |  | 6.5 | 3.5 | 14.4 | 9.6
65 | 210 | 460 | 6.7 | 3.3 | 14.7 | 9.3 | 6.7 | 3.3 | 14.7 | 9.3 | 6.7 | 3.3 | 14.7 | 9.3
75 | 260 | 600 | 6.9 | 3.1 | 15 | 9 | 6.9 | 3.1 | 15 | 9 | 6.9 | 3.1 | 15 | 9
85 | 320 | 740 | 7.1 | 2.9 | 15.4 | 8.6 | 7.1 | 2.9 | 15.4 | 8.6 | 7.1 | 2.9 | 15.4 | 8.6
100 | 380 | 910 | 7.3 | 2.7 | 15.7 | 8.3 | 7.3 | 2.7 | 15.7 | 8.3 | 7.3 | 2.7 | 15.7 | 8.3
120 | 430 | 1110 | 7.6 | 2.4 | 16.2 | 7.8 | 7.6 | 2.4 | 16.2 | 7.8 | 7.6 | 2.4 | 16.2 | 7.8
140 | 490 | 1310 | 7.8 | 2.2 | 16.5 | 7.5 | 7.8 | 2.2 | 16.5 | 7.5 | 7.8 | 2.2 | 16.5 | 7.5
190 | 550 | 1540 | 8 | 2 | 16.8 | 7.2 | 8 | 2 | 16.8 | 7.2 | 8 | 2 | 16.8 | 7.2
240 | 610 | 1760 | 8.2 | 1.8 | 17.1 | 6.9 | 8.2 | 1.8 | 17.1 | 6.9 | 8.2 | 1.8 | 17.1 | 6.9
310 | 700 | 2020 | 8.4 | 1.6 | 17.4 | 6.6 | 8.4 | 1.6 | 17.4 | 6.6 | 8.4 | 1.6 | 17.4 | 6.6
380 | 810 | 2310 | 8.7 | 1.3 | 17.9 | 6.1 | 8.7 | 1.3 | 17.9 | 6.1 | 8.7 | 1.3 | 17.9 | 6.1
460 | 910 | 2600 | 8.9 | 1.1 | 18.2 | 5.8 | 8.9 | 1.1 | 18.2 | 5.8 | 8.9 | 1.1 | 18.2 | 5.8
560 | 1000 | 3000 | 9.1 | 0.9 | 18.6 | 5.4 | 9.1 | 0.9 | 18.6 | 5.4 | 9.1 | 0.9 | 18.6 | 5.4
660 | 1090 | 3400 | 9.3 | 0.7 | 18.9 | 5.1 | 9.3 | 0.7 | 18.9 | 5.1 | 9.3 | 0.7 | 18.9 | 5.1
730 | 1150 | 3730 | 9.5 | 0.5 | 19.2 | 4.8 | 9.5 | 0.5 | 19.2 | 4.8 | 9.5 | 0.5 | 19.2 | 4.8
780 | 1170 | 3990 | 9.8 | 0.2 | 19.7 | 4.3 | 9.8 | 0.2 | 19.7 | 4.3 | 9.8 | 0.2 | 19.7 | 4.3
830 | 1200 | 4250 | 10 | 0 | 20 | 4 | 10 | 0 | 20 | 4 | 10 | 0 | 20 | 4

## OPTIMIZER 6 way
QUICK - CALC OPTIMIZER 6-Way
Setting & Selection program
Input
Flow cooling | 3609 | l/h
Flow heating | 3609 | l/h
OPTIMA Compact
Dimension | Range |  | Calculation cooling |  | Total OPTIMIZER | Calculation heating
| Flow l/h | Range ∆Pp (kPa) | Pre-set | Min. ∆P (kPa) | Min. ∆P (kPa) | Pre-set
DN15 Low 5,0 | 65-370 | 14-600 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
DN15 High 5,0 | 220-1330 | 16-600 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
DN20 High 5,5 | 300-1800 | 18-600 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
DN25L 5,5 | 600-3609 | 17-800 | 4.0002 | 22.9968 | 95.1068 | 100%
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
Type | Min | Max | Evaluering af Flow
DN15 Low 5,0 | 65 | 370 | UDEN FOR OMRÅDET
DN15 High 5,0 | 220 | 1330 | UDEN FOR OMRÅDET
DN 20 High 5,5 | 300 | 1800 | UDEN FOR OMRÅDET
DN25 | 600 | 3609 | 3609

## ALPHA
Quick - CALC Frese ALPHA
Selection program
|  |  | Input |  | CARTRIDGE SELECTION |  |  |  | Flow | Min. ΔP | Item no. | Item no. | Deviation
| Input Q = |  | 6700 | (l/h) Flow | with selected Valve dimension (DN) |  |  |  | l/h | kPa | LP | HP
| ΔP range (kPa) | DN15-25 | DN25L-50 |  | Nearest higher Flow |  |  |  | 6813 | 27 | 50-44200 | 49-44200 | 1.687%
| LP Low Press. | 7-350 | 12-350
| HP High Press. | 7-600 | 12-600 |  | Nearest lower Flow |  |  |  | 6360 | 26 | 50-44194 | 49-44194 | -5.075%
[7 empty] | Plugs |  | Drain Valve |  | P/T-Plugs
| Dimension Valve house DN | [5 empty] | ALPHA | Item no. | ALPHA | Item no. | ALPHA | Item no.
| Input DN = |  | 50 |  |  |  | 50 | 49-9066 | 50 | 49-9064 | 50 | 49-9061
ALPHA Valve
| Valve | Flow
| Dimension | range
| DN | l/h
| 15 | 25-2448
| 20 | 25-2448
| 25 | 25-2448
| 25L | 674-11355
| 32 | 674-11355
| 40 | 674-11355
| 50 | 674-11355
| Alpha Regler |  | Berechnung nächst kleiner Volumenstrom |  |  |  | Berechnung nächst größer Volumenstrom |  |  |  | Alpha Ventilgehäuse Modell
| Ventil | Vol.- | Vol.- | Min. ΔP | Art.-Nr. | Art.-Nr. | Vol.- | Min. ΔP | Art.-Nr. | Art.-Nr. | Art.-Nr. | Art.-Nr. | Art.-Nr.
| Dimension | Bereich | Strom |  | LP-Einsatz | HP-Einsatz | Strom |  | LP-Einsatz | HP-Einsatz | Alpha S | Alpha FE | Alpha DM
| DN | L/h | L/h | kPa | bis 3,5 bar | bis 6,0 bar | L/h | kPa | bis 3,5 bar | bis 6,0 bar | IG/IG | IG/IG | IG/IG
| 15 | 25-2448 | 2448 | 28 | 50-21090 | 49-21090 | 2448 | 28 | 50-21090 | 49-21090 | 49-9006 | 49-9004 | 49-9001
| 20 | 25-2448 | 2448 | 28 | 50-21090 | 49-21090 | 2448 | 28 | 50-21090 | 49-21090 | 49-9016 | 49-9014 | 49-9011
| 25 | 25-2448 | 2448 | 28 | 50-21090 | 49-21090 | 2448 | 28 | 50-21090 | 49-21090 | 49-9026 | 49-9024 | 49-9021
| 25L | 674-11355 | 6360 | 26 | 50-44194 | 49-44194 | 6813 | 27 | 50-44200 | 49-44200 | 49-9036 | 49-9034 | 49-9031
| 32 | 674-11355 | 6360 | 26 | 50-44194 | 49-44194 | 6813 | 27 | 50-44200 | 49-44200 | 49-9046 | 49-9044 | 49-9041
| 40 | 674-11355 | 6360 | 26 | 50-44194 | 49-44194 | 6813 | 27 | 50-44200 | 49-44200 | 49-9056 | 49-9054 | 49-9051
| 50 | 674-11355 | 6360 | 26 | 50-44194 | 49-44194 | 6813 | 27 | 50-44200 | 49-44200 | 49-9066 | 49-9064 | 49-9061
| DN15-DN25 | [7 empty] | DN25L-DN50 | [7 empty] | Gehäuse sind mit Stopfen, Druckmessnippel oder Füll- und Entleerungskugelhahn
| Kleiner |  |  |  | Grosser |  |  |  | Kleiner |  |  |  | Grosser
| L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | Der Regelbereich = S ….
|  | DP | LP | HP |  | DP | LP | HP |  | DP | LP | HP |  | DP | LP | HP
| 0 |  |  |  | 25 | 7 | 50-11150 | N/A | 0 |  |  |  | 674 | 12 | 50-33073 | 49-33073
| 25 | 7 | 50-11150 | N/A | 36 | 7 | 50-11170 | N/A | 674 | 12 | 50-33073 | 49-33073 | 861 | 12 | 50-33082 | 49-33082
| 36 | 7 | 50-11170 | N/A | 43 | 7 | 50-11190 | N/A | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089
| 43 | 7 | 50-11190 | N/A | 55 | 7 | 50-11210 | 49-11210 | 1020 | 12 | 50-33089 | 49-33089 | 1136 | 12 | 50-33094 | 49-33094
| 55 | 7 | 50-11210 | 49-11210 | 75 | 8 | 50-11230 | 49-11230 | 1136 | 12 | 50-33094 | 49-33094 | 1190 | 12 | 50-33096 | 49-33096
| 75 | 8 | 50-11230 | 49-11230 | 84 | 9 | 50-11260 | 49-11260 | 1190 | 12 | 50-33096 | 49-33096 | 1272 | 13 | 50-33098 | 49-33098
| 84 | 9 | 50-11260 | 49-11260 | 104 | 10 | 50-11290 | 49-11290 | 1272 | 13 | 50-33098 | 49-33098 | 1349 | 13 | 50-33102 | 49-33102
| 104 | 10 | 50-11290 | 49-11290 | 114 | 10 | 50-11300 | 49-11300 | 1349 | 13 | 50-33102 | 49-33102 | 1485 | 13 | 50-33107 | 49-33107
| 114 | 10 | 50-11300 | 49-11300 | 129 | 11 | 50-11320 | 49-11320 | 1485 | 13 | 50-33107 | 49-33107 | 1567 | 14 | 50-33111 | 49-33111
| 129 | 11 | 50-11320 | 49-11320 | 154 | 11 | 50-11350 | 49-11350 | 1567 | 14 | 50-33111 | 49-33111 | 1631 | 14 | 50-33112 | 49-33112
| 154 | 11 | 50-11350 | 49-11350 | 175 | 12 | 50-11370 | 49-11370 | 1631 | 14 | 50-33112 | 49-33112 | 1815 | 14 | 50-33118 | 49-33118
| 175 | 12 | 50-11370 | 49-11370 | 204 | 12 | 50-11400 | 49-11400 | 1815 | 14 | 50-33118 | 49-33118 | 2001 | 15 | 50-33124 | 49-33124
| 204 | 12 | 50-11400 | 49-11400 | 241 | 12 | 50-11430 | 49-11430 | 2001 | 15 | 50-33124 | 49-33124 | 2044 | 16 | 50-33125 | 49-33125
| 241 | 12 | 50-11430 | 49-11430 | 279 | 12 | 50-11460 | 49-11460 | 2044 | 16 | 50-33125 | 49-33125 | 2171 | 16 | 50-33129 | 49-33129
| 279 | 12 | 50-11460 | 49-11460 | 320 | 13 | 50-11490 | 49-11490 | 2171 | 16 | 50-33129 | 49-33129 | 2271 | 17 | 50-33132 | 49-33132
| 320 | 13 | 50-11490 | 49-11490 | 350 | 13 | 50-11510 | 49-11510 | 2271 | 17 | 50-33132 | 49-33132 | 2380 | 17 | 50-33135 | 49-33135
| 350 | 13 | 50-11510 | 49-11510 | 400 | 13 | 50-11540 | 49-11540 | 2380 | 17 | 50-33135 | 49-33135 | 2498 | 18 | 50-33138 | 49-33138
| 400 | 13 | 50-11540 | 49-11540 | 477 | 14 | 50-11570 | 49-11570 | 2498 | 18 | 50-33138 | 49-33138 | 2639 | 18 | 50-33142 | 49-33142
| 477 | 14 | 50-11570 | 49-11570 | 545 | 14 | 50-11620 | 49-11620 | 2639 | 18 | 50-33142 | 49-33142 | 2871 | 19 | 50-33148 | 49-33148
| 545 | 14 | 50-11620 | 49-11620 | 615 | 14 | 50-11725 | 49-11725 | 2871 | 19 | 50-33148 | 49-33148 | 3191 | 21 | 50-33156 | 49-33156
| 615 | 14 | 50-11725 | 49-11725 | 670 | 14 | 50-11730 | 49-11730 | 3191 | 21 | 50-33156 | 49-33156 | 3407 | 22 | 50-33161 | 49-33161
| 670 | 14 | 50-11730 | 49-11730 | 736 | 14 | 50-11735 | 49-11735 | 3407 | 22 | 50-33161 | 49-33161 | 3486 | 22 | 50-33163 | 49-33163
| 736 | 14 | 50-11735 | 49-11735 | 799 | 16 | 50-11740 | 49-11740 | 3486 | 22 | 50-33163 | 49-33163 | 3634 | 20 | 50-44148 | 49-44148
| 799 | 16 | 50-11740 | 49-11740 | 870 | 19 | 50-11745 | 49-11745 | 3634 | 20 | 50-44148 | 49-44148 | 3860 | 21 | 50-44152 | 49-44152
| 870 | 19 | 50-11745 | 49-11745 | 936 | 21 | 50-11750 | 49-11750 | 3860 | 21 | 50-44152 | 49-44152 | 4088 | 21 | 50-44156 | 49-44156
| 936 | 21 | 50-11750 | 49-11750 | 1020 | 22 | 50-20700 | 49-20700 | 4088 | 21 | 50-44156 | 49-44156 | 4315 | 21 | 50-44164 | 49-44164
| 1020 | 22 | 50-20700 | 49-20700 | 1081 | 22 | 50-20740 | 49-20740 | 4315 | 21 | 50-44164 | 49-44164 | 4542 | 22 | 50-44168 | 49-44168
| 1081 | 22 | 50-20740 | 49-20740 | 1195 | 22 | 50-20770 | 49-20770 | 4542 | 22 | 50-44168 | 49-44168 | 4769 | 22 | 50-44173 | 49-44173
| 1195 | 22 | 50-20770 | 49-20770 | 1335 | 23 | 50-20820 | 49-20820 | 4769 | 22 | 50-44173 | 49-44173 | 4996 | 23 | 50-44176 | 49-44176
| 1335 | 23 | 50-20820 | 49-20820 | 1483 | 23 | 50-20860 | 49-20860 | 4996 | 23 | 50-44176 | 49-44176 | 5450 | 24 | 50-44182 | 49-44182
| 1483 | 23 | 50-20860 | 49-20860 | 1581 | 23 | 50-20880 | 49-20880 | 5450 | 24 | 50-44182 | 49-44182 | 5905 | 25 | 50-44191 | 49-44191
| 1581 | 23 | 50-20880 | 49-20880 | 1774 | 24 | 50-20920 | 49-20920 | 5905 | 25 | 50-44191 | 49-44191 | 6360 | 26 | 50-44194 | 49-44194
| 1774 | 24 | 50-20920 | 49-20920 | 1883 | 24 | 50-20940 | 49-20940 | 6360 | 26 | 50-44194 | 49-44194 | 6813 | 27 | 50-44200 | 49-44200
| 1883 | 24 | 50-20940 | 49-20940 | 2080 | 25 | 50-20990 | 49-20990 | 6813 | 27 | 50-44200 | 49-44200 | 7267 | 28 | 50-44205 | 49-44205
| 2080 | 25 | 50-20990 | 49-20990 | 2251 | 26 | 50-21030 | 49-21030 | 7267 | 28 | 50-44205 | 49-44205 | 7721 | 30 | 50-44211 | 49-44211
| 2251 | 26 | 50-21030 | 49-21030 | 2319 | 27 | 50-21060 | 49-21060 | 7721 | 30 | 50-44211 | 49-44211 | 8176 | 31 | 50-44217 | 49-44217
| 2319 | 27 | 50-21060 | 49-21060 | 2448 | 28 | 50-21090 | 49-21090 | 8176 | 31 | 50-44217 | 49-44217 | 8630 | 33 | 50-44222 | 49-44222
| 2448 | 28 | 50-21090 | 49-21090 | 2448 | 28 | 50-21090 | 49-21090 | 8630 | 33 | 50-44222 | 49-44222 | 9084 | 34 | 50-44229 | 49-44229
[9 empty] | 9084 | 34 | 50-44229 | 49-44229 | 9538 | 36 | 50-44235 | 49-44235
[9 empty] | 9538 | 36 | 50-44235 | 49-44235 | 9990 | 38 | 50-44241 | 49-44241
[9 empty] | 9990 | 38 | 50-44241 | 49-44241 | 10445 | 40 | 50-44248 | 49-44248
[9 empty] | 10445 | 40 | 50-44248 | 49-44248 | 10900 | 42 | 50-44250 | 49-44250
[9 empty] | 10900 | 42 | 50-44250 | 49-44250 | 11355 | 44 | 50-44262 | 49-44262
[9 empty] | 11355 | 44 | 50-44262 | 49-44262 | 11355 | 44 | 50-44262 | 49-44262

## ALPHA Wafer
QUICK - CALC Frese ALPHA Wafer
Selection program
|  |  | Input |  | CARTRIDGE SELECTION |  |  | Flow | Min. ΔP | Qty | Vare nr. | Flow |  | Qty | Item no. | Flow | Deviation
| Input Q = |  | 5000 | m³/h Flow | with selected Valve dimension |  |  | m³/h | kPa | Cartriges |  |  |  | Cartridges
[5 empty] | Nearest higher Flow |  |  | 675 | 49 | 13 | 52-66407H | 45 |  | 2 | 52-66407H | 45 | -86.5%
Cartridge Type HP (High Pressure)
| AISI 304 |  |  |  | Nearest lower Flow |  |  | 675 | 49 | 15 | 52-66407H | 45 |  |  |  |  | -86.5%
ΔP range: 13 - 600 kPa
Dimension Valve house DN
| Input DN = |  | 300
| Item no. Valve house |  | 49-9143-01
|  |  | Berechnungen Nächst kleiner Volumenstrom : |  |  |  |  | Berechnungen Nächst größer Volumenstrom :
Ventil | Vol.-Ber. | Anzahl | Vol.-Str | Min ΔP | Art.-Nr. | Vol.-Strom | Ist/Soll | Vol.-Strom | Min. ΔP | Anzahl | Art.-Nr. | Vol.- | Anz | Rest | Art.-Nr. | Vol.- | Ist/Soll
Dim. | m³/h | Einsätze | m³/h | kPa |  | m³/h | Abw. | m³/h | kPa | Einsätze |  | Strom | Eins | Vol.-Str |  | Strom | Abw.
DN |  |  | Regler Komplett |  | Einsatz | Einsatz |  | Regler Komplett |  |  | Einsatz | Eins. |  | m³/h | Einsatz | Eins.
50 | 3,8 - 45 | 1 | 45 | 49 | 52-66407H | 45 | -99.1% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 4955 | 0 | 0 | -99.1%
65 | 3,8 - 45 | 1 | 45 | 49 | 52-66407H | 45 | -99.1% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 4955 | 0 | 0 | -99.1%
80 | 3,8 - 45 | 1 | 45 | 49 | 52-66407H | 45 | -99.1% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 4955 | 0 | 0 | -99.1%
100 | 3,8 - 90 | 2 | 90 | 49 | 52-66407H | 45 | -98.2% | 90 | 49 | 1 | 52-66407H | 45 | 1 | 4955 | 52-66407H | 45 | -98.2%
125 | 3,8 - 135 | 3 | 135 | 49 | 52-66407H | 45 | -97.3% | 135 | 49 | 2 | 52-66407H | 45 | 1 | 4910 | 52-66407H | 45 | -97.3%
150 | 3,8 - 180 | 4 | 180 | 49 | 52-66407H | 45 | -96.4% | 180 | 49 | 3 | 52-66407H | 45 | 1 | 4865 | 52-66407H | 45 | -96.4%
200 | 3,8 - 315 | 7 | 315 | 49 | 52-66407H | 45 | -93.7% | 315 | 49 | 6 | 52-66407H | 45 | 1 | 4730 | 52-66407H | 45 | -93.7%
250 | 3,8 - 540 | 12 | 540 | 49 | 52-66407H | 45 | -89.2% | 540 | 49 | 10 | 52-66407H | 45 | 2 | 2275 | 52-66407H | 45 | -89.2%
300 | 3,8 - 675 | 15 | 675 | 49 | 52-66407H | 45 | -86.5% | 675 | 49 | 13 | 52-66407H | 45 | 2 | 2207.5 | 52-66407H | 45 | -86.5%
350 | 3,8 - 855 | 19 | 855 | 49 | 52-66407H | 45 | -82.9% | 855 | 49 | 16 | 52-66407H | 45 | 3 | 1426.6667 | 52-66407H | 45 | -82.9%
400 | 3,8 - 1170 | 26 | 1170 | 49 | 52-66407H | 45 | -76.6% | 1170 | 49 | 21 | 52-66407H | 45 | 5 | 811 | 52-66407H | 45 | -76.6%
450 | 3,8 - 1485 | 33 | 1485 | 49 | 52-66407H | 45 | -70.3% | 1485 | 49 | 23 | 52-66407H | 45 | 10 | 396.5 | 52-66407H | 45 | -70.3%
500 | 3,8 - 1800 | 40 | 1800 | 49 | 52-66407H | 45 | -64% | 1800 | 49 | 30 | 52-66407H | 45 | 10 | 365 | 52-66407H | 45 | -64%
600 | 3,8 - 2520 | 56 | 2520 | 49 | 52-66407H | 45 | -49.6% | 2520 | 49 | 41 | 52-66407H | 45 | 15 | 210.3333 | 52-66407H | 45 | -49.6%
800 | 3,8 - 3825 | 85 | 3825 | 49 | 52-66407H | 45 | -23.5% | 3825 | 49 | 65 | 52-66407H | 45 | 20 | 103.75 | 52-66407H | 45 | -23.5%
900 | 3,8 - 5040 | 112 | 4592 | 46 | 52-66407 | 41 | -8.16% | 5040 | 49 | 92 | 52-66407H | 45 | 20 | 43 | 52-66407H | 45 | 0.8%
1000 | 3,8 - 6120 | 136 | 4936.8 | 42 | 52-66393 | 36.3 | -1.264% | 5019.2 | 43 | 116 | 52-66398 | 37.7 | 20 | 31.34 | 52-66379 | 32.3 | 0.384%
| '=((SVERWEIS(($D$5/$C17);$D$40:$F$84;1)*C17)) | [6 empty] | Flow > | =((SVERWEIS(($D$5/$C22);$C$38:$I$81;1)*(C22-1)))
| '=WENN($D$5/$C23<3,8;SVERWEIS(($D$5/$C22);$D$40:$F$84;1);SVERWEIS(($D$5/$C23);$D$40:$F$84;1)) | [10 empty] | Korrektion til slut :
| '=WENN($D$5/$C24<3,8;D23;SVERWEIS(($D$5/$C24);$D$40:$F$84;1)) | [10 empty] | Spalte D:H Min el slettes
DN50-DN800
|  | Kleiner |  |  |  | Grosser | [5 empty] | WENN(Prüfung;Dann_Wert; WENN(Prüfung;Dann_Wert;Sonst_Wert))
|  | L/h | m³/h | Min |  | m³/h | Min
|  |  |  | DP | Vare nr. |  | DP | Vare nr. |  |  |  | SVERWEIS(Suchkriterium;Matrix;Spalteindex;Bereich_Verweis)
0
|  |  | 0 |  |  | 3.8 | 13 | 52-55179 |  | 45 | D | '=((SVERWEIS(($D$5/$C17);$D$40:$F$84;1)*C17))
|  | 3820 | 3.8 | 13 | 52-55179 | 3.9 | 13 | 52-55184 |  | 49 | E | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;2)
|  | 3931 | 3.9 | 13 | 52-55184 | 4 | 13 | 52-55189 |  | 52-66407H | F | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;3)
|  | 4049 | 4 | 13 | 52-55189 | 4.2 | 13 | 52-55194 |  | 45 | G | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;1)
|  | 4199 | 4.2 | 13 | 52-55194 | 4.4 | 13 | 52-55200
|  | 4399 | 4.4 | 13 | 52-55200 | 4.6 | 14 | 52-55206
|  | 4640 | 4.6 | 14 | 52-55206 | 5 | 14 | 52-55213 |  | WENN(O23<0;
|  | 4951 | 5 | 14 | 52-55213 | 5.3 | 14 | 52-55220
|  | 5310 | 5.3 | 14 | 52-55220 | 5.7 | 14 | 52-55227
|  | 5700 | 5.7 | 14 | 52-55227 | 6.2 | 14 | 52-55235 |  | DN | Art.-Nr. Gehäuse
|  | 6209 | 6.2 | 14 | 52-55235 | 6.5 | 14 | 52-55243 |  | 50 | 49-9073-01
|  | 6511 | 6.5 | 14 | 52-55243 | 7.1 | 14 | 52-55251 |  | 65 | 49-9083-01
|  | 7081 | 7.1 | 14 | 52-55251 | 7.9 | 15 | 52-55260 |  | 80 | 49-9093-01
|  | 7901 | 7.9 | 15 | 52-55260 | 8.9 | 16 | 52-55269 |  | 100 | 49-9103-01
|  | 8900 | 8.9 | 16 | 52-55269 | 10.4 | 19 | 52-55279 |  | 125 | 49-9163-01
|  | 10399 | 10.4 | 19 | 52-55279 | 11.4 | 22 | 52-55287 |  | 150 | 49-9113-01
|  | 11355 | 11.4 | 22 | 52-55287 | 12.5 | 23 | 52-55292 |  | 200 | 49-9123-01
|  | 12491 | 12.5 | 23 | 52-55292 | 13.4 | 24 | 52-55298 |  | 250 | 49-9133-01
|  | 13399 | 13.4 | 24 | 52-55298 | 14.8 | 27 | 52-55303 |  | 300 | 49-9143-01
|  | 14762 | 14.8 | 27 | 52-55303 | 16 | 29 | 52-55308 |  | 350 | 49-9153-01
|  | 15999 | 16 | 29 | 52-55308 | 17 | 34 | 52-66285 |  | 400 | 49-9173-01
|  | 17037 | 17 | 34 | 52-66285 | 18.1 | 34 | 52-66292 |  | 450 | 49-9183-01
|  | 18148 | 18.1 | 34 | 52-66292 | 18.8 | 35 | 52-66301 |  | 500 | 49-9193-01
|  | 18797 | 18.8 | 35 | 52-66301 | 19.5 | 35 | 52-66305 |  | 600 | 49-9203-01
|  | 19467 | 19.5 | 35 | 52-66305 | 20.5 | 35 | 52-66312 |  | 800 | 49-9213-01
|  | 20464 | 20.5 | 35 | 52-66312 | 21.5 | 36 | 52-66319 |  | 900 | 49-9233-01
|  | 21527 | 21.5 | 36 | 52-66319 | 22.4 | 36 | 52-66326 |  | 1000 | 49-9223-01
|  | 22449 | 22.4 | 36 | 52-66326 | 23.5 | 36 | 52-66332
|  | 23482 | 23.5 | 36 | 52-66332 | 24.5 | 37 | 52-66338
|  | 24531 | 24.5 | 37 | 52-66338 | 25.6 | 38 | 52-66344
|  | 25621 | 25.6 | 38 | 52-66344 | 26.5 | 38 | 52-66349
|  | 26528 | 26.5 | 38 | 52-66349 | 27.7 | 38 | 52-66356
|  | 27686 | 27.7 | 38 | 52-66356 | 29.2 | 38 | 52-66362
|  | 29157 | 29.2 | 38 | 52-66362 | 30 | 39 | 52-66367
|  | 29954 | 30 | 39 | 52-66367 | 31 | 39 | 52-66373
|  | 30976 | 31 | 39 | 52-66373 | 32.3 | 40 | 52-66379
|  | 32260 | 32.3 | 40 | 52-66379 | 33.6 | 40 | 52-66385
|  | 33565 | 33.6 | 40 | 52-66385 | 35 | 40 | 52-66391
|  | 34953 | 35 | 40 | 52-66391 | 36.3 | 42 | 52-66393
|  | 36336 | 36.3 | 42 | 52-66393 | 37.7 | 43 | 52-66398
|  | 37685 | 37.7 | 43 | 52-66398 | 38.6 | 44 | 52-66400
|  | 38607 | 38.6 | 44 | 52-66400 | 41 | 46 | 52-66407
|  | 40971 | 41 | 46 | 52-66407 | 45 | 49 | 52-66407H
|  | 45000 | 45 | 49 | 52-66407H | 45 | 49 | 52-66407H
Valve | Flow | Qty
Dim. | m³/h | Cartridges
DN
50 | 3,8 - 45 | 1
65 | 3,8 - 45 | 1
80 | 3,8 - 45 | 1
100 | 3,8 - 90 | 2
125 | 3,8 - 135 | 3
150 | 3,8 - 180 | 4
200 | 3,8 - 315 | 7
250 | 3,8 - 540 | 12
300 | 3,8 - 675 | 15
350 | 3,8 - 855 | 19
400 | 3,8 - 1170 | 26
450 | 3,8 - 1485 | 33
500 | 3,8 - 1800 | 40
600 | 3,8 - 2520 | 56
800 | 3,8 - 3825 | 85
900 | 3,8 - 5040 | 112
1000 | 3,8 - 6120 | 136

## SIGMA Compact
QUICK - CALC SIGMA Compact
Setting & Selection program
Input Q = | 1500 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp (kPa) | Pre-set | Kv | Min. ∆P (kPa)
DN15 Low | 40-900 | 10-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN15 High | 60-1080 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 Low | 86-1550 | 9-400 | 3.569 | 1.196 | 13.526
DN20 High | 102-1930 | 16-400 | 2.8 | 0.92688 | 18.352
DN25 Low | 95-2000 | 10-400 | 2.9 |  | 20.72
DN25 High | 137-2400 | 14-400 | 2.4 | 1.0696 | 17.1032
DN25L (53-2204 withdrawn) | 150-1930 | 17-400 | 2.9996 | 1.4841 | 11.8079
DN32 | 200-5000 | 15-400 | 1.3716 | 1.0133 | 15.832
DN40 | 719-7400 | 10-400 | 0.94385 | 0.39399 | 10
DN50 | 900-10350 | 10-400 | 0.8 | 0.53997 | 10
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
Type | Min | Max | Evaluering Flow
DN15 LF | 40 | 900 | UDEN FOR OMRÅDET
DN15 HF | 60 | 1080 | UDEN FOR OMRÅDET
DN20 LF | 86 | 1550 | 1500
DN20 HF | 102 | 1930 | 1500
DN25 LF | 95 | 2000 | 1500
DN25 HF | 137 | 2400 | 1500
DN25L (53-2204 withdrawn) | 150 | 1930 | 1500
DN32 | 200 | 5000 | 1500
DN40 | 719 | 7400 | 1500
DN50 | 900 | 10350 | 1500

## SIGMA Compact Flanged
QUICK - CALC SIGMA Compact Flanged
Setting & Selection program
Input
Input Q = | 10.5 | (m3/h) Flow
Dimension & Type | Range |  | Calculation
| Flow (m3/h) | Range ∆Pp(kPa) | Pre-set | Min. ∆P (kPa)
DN50 Ultra High Flow | 1.40-11.5 | 10-800 | 3.8244 | 33.6931
DN50 Standard Low Flow | 2.50-15.0 | 7-800 | 3.0743 | 12.4383
DN50 Standard High Flow | 3.90-24.0 | 19-800 | 1.8612 | 20.3949
DN65 Ultra Low Flow | 3.00-16.0 | 10-800 | 2.8462 | 11.7117
DN65 Ultra High Flow | 4.20-24.0 | 19-800 | 1.839 | 19.7833
DN65 Standard Low Flow | 4.40-25.0 | 15-800 | 1.7931 | 17.5931
DN65 Standard High Flow | 6.00-35.0 | 30-800 | 1.1976 | 31.0776
DN80 Ultra Low Flow | 4.40-25.0 | 15-800 | 1.7946 | 17.3711
DN80 Ultra High Flow | 6.00-35.0 | 30-800 | 1.2023 | 27
DN80 Standard Low Flow | 5.30-34.0 | 16-800 | 1.3573 | 9
DN80 Standard High Flow | 7.00-43.0 | 23-800 | 0.94888 | 15
DN100 Ultra Low Flow | 5.30-34.0 | 16-800 | 1.3325 | 9
DN100 Ultra High Flow | 7.00-43.0 | 23-800 | 0.9458 | 15
DN100 Standard Low Flow | 12.1-68.0 | 20-800 | NOT POSSIBLE | NOT POSSIBLE
DN100 Standard High Flow | 14.8-90.0 | 30-800 | NOT POSSIBLE | NOT POSSIBLE
DN125 Ultra Low Flow | 12.1-68.0 | 20-800 | NOT POSSIBLE | NOT POSSIBLE
DN125 Ultra High Flow | 14.8-90.0 | 30-800 | NOT POSSIBLE | NOT POSSIBLE
DN125 Standard Low Flow | 18.5-110 | 16-800 | NOT POSSIBLE | NOT POSSIBLE
DN125 Standard High Flow | 23.0-135 | 27-800 | NOT POSSIBLE | NOT POSSIBLE
DN150 Standard Low Flow | 25.6-148 | 21-800 | NOT POSSIBLE | NOT POSSIBLE
DN150 Standard High Flow | 32.0-195 | 33-800 | NOT POSSIBLE | NOT POSSIBLE
DN200 Standard Low Flow | 95.0-210 | 11-800 | NOT POSSIBLE | NOT POSSIBLE
DN200 Standard High Flow | 130-280 | 31-800 | NOT POSSIBLE | NOT POSSIBLE
DN250 Standard Low Flow | 190-475 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
DN250 Standard High Flow | 245-600 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN300 Standard Low Flow | 190-475 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
DN300 Standard High Flow | 245-600 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
Type | Min | Max | Evaluering Flow
DN50 Ultra High Flow | 1.4 | 11.5 | 10.5
DN50 Standard Low Flow | 2.5 | 15 | 10.5
DN50 Standard High Flow | 3.9 | 24 | 10.5
DN65 Ultra Low Flow | 3 | 16 | 10.5
DN65 Ultra High Flow | 4.2 | 24 | 10.5
DN65 Standard Low Flow | 4.4 | 25 | 10.5
DN65 Standard High Flow | 6 | 35 | 10.5
DN80 Ultra Low Flow | 4.4 | 25 | 10.5
DN80 Ultra High Flow | 6 | 35 | 10.5
DN80 Standard Low Flow | 5.3 | 34 | 10.5
DN80 Standard High Flow | 7 | 43 | 10.5
DN100 Ultra Low Flow | 5.3 | 34 | 10.5
DN100 Ultra High Flow | 7 | 43 | 10.5
DN100 Standard Low Flow | 12.1 | 68 | UDEN FOR OMRÅDET
DN100 Standard High Flow | 14.8 | 90 | UDEN FOR OMRÅDET
DN125 Ultra Low Flow | 12.1 | 68 | UDEN FOR OMRÅDET
DN125 Ultra High Flow | 14.8 | 90 | UDEN FOR OMRÅDET
DN125 Standard Low Flow | 18.5 | 110 | UDEN FOR OMRÅDET
DN125 Standard High Flow | 23 | 135 | UDEN FOR OMRÅDET
DN150 Standard Low Flow | 25.6 | 148 | UDEN FOR OMRÅDET
DN150 Standard High Flow | 32 | 195 | UDEN FOR OMRÅDET
DN200 Standard Low Flow | 95 | 210 | UDEN FOR OMRÅDET
DN200 Standard High Flow | 130 | 280 | UDEN FOR OMRÅDET
DN250 Standard Low Flow | 190 | 475 | UDEN FOR OMRÅDET
DN250 Standard High Flow | 245 | 600 | UDEN FOR OMRÅDET
DN300 Standard Low Flow | 190 | 475 | UDEN FOR OMRÅDET
DN300 Standard High Flow | 245 | 600 | UDEN FOR OMRÅDET

## PV Compact
QUICK - CALC Frese PV Compact
Setting & Selection program
Input
Input ∆Ps = |  | 20 | (kPa) Differential Pessure setting
Input Q = |  | 500 | (l/h) Design flow
Dim. | ∆Ps range | Range |  | Pre-set
|  | Flow (l/h) | Range ∆Pp (kPa) | Number of turns
DN15 | 5-30 kPa | 50-600 | 5-450 | 11.8382
DN15 | 20-60 kPa | 100-1000 | 20-450 | 1.3
DN20 | 5-30 kPa | 100-1000 | 5-450 | 11.8382
DN20 | 20-60 kPa | 150-2000 | 20-450 | 1.2974
DN25 | 5-30 kPa | 600-2100 | 5-450 | NOT POSSIBLE
DN25L | 20-80 kPa | 750-4200 | 20-450 | NOT POSSIBLE
DN32 | 20-80 kPa | 1000-5000 | 20-450 | NOT POSSIBLE
DN40 | 20-80 kPa | 3000-8000 | 20-450 | NOT POSSIBLE
DN50 | 20-80 kPa | 5000-11500 | 20-450 | NOT POSSIBLE
DN50 Ultra | 20-80 kPa | 3200-13000 | 20-450 | NOT POSSIBLE
Calculation of pressure loss
Dimension |  | ∆Pv (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa |  | 2.9727 | 22.9727
DN15 20-60 kPa |  | 2.9727 | 22.9727
DN20 5-30 kPa |  | 2.0408 | 22.0408
DN20 20-60 kPa |  | 2.0408 | 22.0408
DN25 5-30 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN25 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN32 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN40 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN50 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN50 Ultra 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa |  | 5 | 272 | 0.68 | 2.9 | 50 | 600 | 500 | 20
DN15 20-60 kPa |  | 20 | 312.5 | 0.4015 | 2.9 | 100 | 1000 | 500 | 20
DN20 5-30 kPa |  | 5 | 272 | 0.68 | 3.5 | 100 | 1000 | 500 | 20
DN20 20-60 kPa |  | 20 | 313 | 0.402 | 3.5 | 150 | 2000 | 500 | 20
DN25 5-30 kPa |  | 5 | 322 | 0.612 | 4 | 600 | 2100 | UDEN FOR OMRÅDET | 20
DN25 20-80 kPa |  | 20 | 1180 | 0.285 | 8.7 | 750 | 4200 | UDEN FOR OMRÅDET | 20
DN32 20-80 kPa |  | 20 | 1201 | 0.275 | 10.1 | 1000 | 5000 | UDEN FOR OMRÅDET | 20
DN40 20-80 kPa |  | 20 | 2411 | 0.299 | 15.8 | 3000 | 8000 | UDEN FOR OMRÅDET | 20
DN50 20-80 kPa |  | 20 | 1547 | 0.23 | 16.2 | 5000 | 11500 | UDEN FOR OMRÅDET | 20
DN50 Ultra 20-80 kPa |  | 12.5 | 2029 | 0.22 | 18.6 | 3200 | 13000 | UDEN FOR OMRÅDET | 20
|  | Offset | Flow/omdr | DP/omdr
∆Pp = Pump pressure
∆Ps = Differential pressure setting
∆Pv = Pressure loss across valve

## PV-SIGMA
QUICK - CALC PV-SIGMA Compact | [9 empty] | QUICK - CALC Frese S
Setting & Selection program | [9 empty] | Auslegungsprogramm für Frese S Dynamischer Volumenstromregler
| Input | [9 empty] | Eingabe
Input ∆Ps = | 30 | (kPa) Differential pressure in system | [7 empty] | Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 1300 | (l/h) Design flow in system | [7 empty] | Eingabe Q = | 25 | (l/h) Auslegungsvolumenstrom | (L/h) Auslegungsvolumenstrom
PV Compact (Return) |  | SIGMA Compact (Supply) |  |  |  | PV-SIGMA System
Pre-set PV Compact |  | Pre-set SIGMA Compact |  |  |  | Total pressure loss
Dimension | Number of turns | Dimension | Pre-set |  | Min. ∆P (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa | NOT POSSIBLE | DN15 Low | NOT POSSIBLE |  | #VALUE! | NOT POSSIBLE
DN15 20-60 kPa | NOT POSSIBLE | DN15 High | NOT POSSIBLE |  | #VALUE! | NOT POSSIBLE
DN20 5-30kPa | NOT POSSIBLE | DN20 Low | 2.8416 |  | 11.5 | NOT POSSIBLE
DN20 20-60kPa | 7.8734 | DN20 High | 2.3 |  | 16.7 | 60.4959
DN25 5-30 kPa | 17.4435 | DN25 High | 2.1 |  | 15.6 | 56.1625
DN25 20-80 kPa | 3.3017 | DN25 High | 2.1 |  | 15.6 | 47.8328
DN32 20-80 kPa | 2.9624 | DN32 | 1.2358 |  | 15.7 | 47.3567
DN40 20-80 kPa | NOT POSSIBLE | DN40 | 0.82826 |  | 10 | NOT POSSIBLE
DN50 20-80 kPa | NOT POSSIBLE | DN50 | 0.7 |  | 10 | NOT POSSIBLE
∆P-PV (kPa)
NOT POSSIBLE
NOT POSSIBLE
NOT POSSIBLE
13.7959
10.5625
2.2328
1.6567
NOT POSSIBLE
NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
| PV Compact ∆P - Controller |  | SIGMA Compact Flow Controller |  |  |  | PV-SIGMA Compact System ∆P & Flow controller
Dim. ∆Ps Range | Flow range (l/h) | ∆Pp range (kPa) | Flow range (l/h) |  |  | ∆Pp range (kPa) | ∆Ps range (kPa) | Flow range (l/h) | ∆Pp range (kPa)
DN15 5-30kPa | 50-600 | 7-450 | 40-900 |  |  | 10-400 | 5-30 | 50-600 | 10-400
DN15 20-60kPa | 100-1000 | 22-450 | 60-1080 |  |  | 14-400 | 20-60 | 100-1000 | 22-400
DN20 5-30 kPa | 100-1000 | 7-450 | 86-1550 |  |  | 9-400 | 5-30 | 100-1000 | 9-400
DN20 20-60 kPa | 150-2000 | 22-450 | 102-1930 |  |  | 16-400 | 20-60 | 150-1930 | 22-400
DN25 5-30kPa | 600-2100 | 7-450 | 137-2400 |  |  | 14-400 | 5-30 | 600-2100 | 14-400
DN25 20-80kPa | 750-4200 | 22-450 | 137-2400 |  |  | 14-400 | 20-80 | 750-2400 | 22-400
DN32 20-80kPa | 1000-5000 | 22-450 | 200-5000 |  |  | 15-400 | 20-80 | 1000-5000 | 22-400
DN40 20-80kPa | 3000-8000 | 22-450 | 719-7400 |  |  | 10-400 | 20-80 | 3000-7400 | 22-400
DN50 20-80kPa | 5000-11500 | 22-450 | 900-10350 |  |  | 10-400 | 20-80 | 5000-10350 | 22-400 | Der Regelbereich ist definiert von Min. Pumpendruck (Min. ∆Pp) bis Max. Pumpendruck (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN | [9 empty] | ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  | X (min Kpa) | Y (Flow/Omdr) | Z (Omdr/kpa) | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp | Type | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa |  | 5 | 272 | 0.68 | 2.9 | 50 | 600 | UDEN FOR OMRÅDET | 30 | DN15 LF |  |  |  | 2.6 | 40 | 900 | UDEN FOR OMRÅDET | 30
DN15 20-60 kPa |  | 20 | 312.5 | 0.4015 | 2.9 | 100 | 1000 | UDEN FOR OMRÅDET | 30 | DN15 HF |  |  |  | 2.6 | 60 | 1080 | UDEN FOR OMRÅDET | 30
DN20 5-30 kPa |  | 5 | 272 | 0.68 | 3.5 | 100 | 1000 | UDEN FOR OMRÅDET | 30 | DN20 LF |  |  |  | 4 | 86 | 1550 | 1300 | 30
DN20 20-60 kPa |  | 20 | 313 | 0.402 | 3.5 | 150 | 2000 | 1300 | 30 | DN20 HF |  |  |  | 4 | 102 | 1930 | 1300 | 30
DN25 5-30 kPa |  | 5 | 321.5 | 0.612 | 4 | 600 | 2100 | 1300 | 30 | DN25 HF |  |  |  | 4.2 | 137 | 2400 | 1300 | 30
DN25 20-80 kPa |  | 20 | 1180 | 0.285 | 8.7 | 750 | 4200 | 1300 | 30 | DN25 HF |  |  |  | 4.2 | 137 | 2400 | 1300 | 30
DN32 20-80 kPa |  | 20 | 1201 | 0.275 | 10.1 | 1000 | 5000 | 1300 | 30 | DN32 |  |  |  | 10.9 | 200 | 5000 | 1300 | 30
DN40 20-80 kPa |  | 20 | 2410.7 | 0.2988 | 15.8 | 3000 | 8000 | UDEN FOR OMRÅDET | 30 | DN40 |  |  |  | 18 | 719 | 7400 | 1300 | 30
DN50 20-80 kPa |  | 20 | 1547 | 0.23 | 16.2 | 5000 | 11500 | UDEN FOR OMRÅDET | 30 | DN50 |  |  |  | 20.3 | 900 | 10350 | 1300 | 30
∆Pp = Pump pressure
∆Ps = Differential pressure in system
∆Pv = Pressure loss across valve
Frese SIGMA Compact (Supply)
Frese PV Compact (Return)
Frese PV Compact
Frese SIGMA Compact
∆Pv
∆Pv
∆Ps
∆Pp
∆Pp = ∆Ps + ∆Pv

## Frese VODRV
QUICK - CALC Frese STBV, VODRV
Setting & Selection program
Input
Input Q: |  | 5000 | (l/h) Flow
Measured diff. Pressure |  | 10 | (kPa) ∆P Signal (For flow measurement)
Kv Signal: (Required) |  | 15.8114
DN | KV signal (Fully open valve) |  | Pre-set |  | KV Total valve |  | Pressureloss (kPa) Total valve (For pump dimensioning)
15 | 6.8 |  | NOT POSSIBLE |  | NOT POSSIBLE |  | NOT POSSIBLE
20 | 9.9 |  | NOT POSSIBLE |  | NOT POSSIBLE |  | NOT POSSIBLE
25 | 31.8 |  | 1.9 |  | 7.378 |  | 45.9264
32 | 23 |  | 2.4 |  | 14.784 |  | 11.4382
40 | 40 |  | 1.6 |  | 13.736 |  | 13.2501
50 | 49.7 |  | 1.3 |  | 15.49 |  | 10.4193
DN 15 |  |  | DN20 |  |  | DN25 |  |  | DN32 |  |  | DN40 |  |  | DN50
KV signal | KV total | Einstellung | KV signal | KV total | Einstellung | KV signal | KV total | Einstellung | KV signal | KV total | Einstellung | KV signal | KV total | Einstellung | KV signal | KV total | Einstellung
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.2 | 0.19 | 0.1 | 0.328 | 0.316 | 0.1 | 0.548 | 0.5 | 0.1 | 0.726 | 0.72 | 0.1 | 0.576 | 0.568 | 0.1 | 1.088 | 1.112 | 0.1
0.4 | 0.38 | 0.2 | 0.656 | 0.632 | 0.2 | 1.096 | 1 | 0.2 | 1.452 | 1.44 | 0.2 | 1.152 | 1.136 | 0.2 | 2.176 | 2.224 | 0.2
0.6 | 0.57 | 0.3 | 0.984 | 0.948 | 0.3 | 1.644 | 1.5 | 0.3 | 2.178 | 2.16 | 0.3 | 1.728 | 1.704 | 0.3 | 3.264 | 3.336 | 0.3
0.8 | 0.76 | 0.4 | 1.312 | 1.264 | 0.4 | 2.192 | 2 | 0.4 | 2.904 | 2.88 | 0.4 | 2.304 | 2.272 | 0.4 | 4.352 | 4.448 | 0.4
1 | 0.95 | 0.5 | 1.64 | 1.58 | 0.5 | 2.74 | 2.5 | 0.5 | 3.63 | 3.6 | 0.5 | 2.88 | 2.84 | 0.5 | 5.44 | 5.56 | 0.5
1.124 | 1.058 | 0.6 | 1.884 | 1.786 | 0.6 | 3.4026 | 2.914 | 0.6 | 4.358 | 4.312 | 0.6 | 3.972 | 3.936 | 0.6 | 6.75 | 6.916 | 0.6
1.248 | 1.166 | 0.7 | 2.128 | 1.992 | 0.7 | 4.0652 | 3.328 | 0.7 | 5.086 | 5.024 | 0.7 | 5.064 | 5.032 | 0.7 | 8.06 | 8.272 | 0.7
1.372 | 1.274 | 0.8 | 2.372 | 2.198 | 0.8 | 4.7278 | 3.742 | 0.8 | 5.814 | 5.736 | 0.8 | 6.156 | 6.128 | 0.8 | 9.37 | 9.628 | 0.8
1.496 | 1.382 | 0.9 | 2.616 | 2.404 | 0.9 | 5.3904 | 4.156 | 0.9 | 6.542 | 6.448 | 0.9 | 7.248 | 7.224 | 0.9 | 10.68 | 10.984 | 0.9
1.62 | 1.49 | 1 | 2.86 | 2.61 | 1 | 6.053 | 4.57 | 1 | 7.27 | 7.16 | 1 | 8.34 | 8.32 | 1 | 11.99 | 12.34 | 1
1.724 | 1.572 | 1.1 | 3.05 | 2.784 | 1.1 | 7.0844 | 4.946 | 1.1 | 8.018 | 7.822 | 1.1 | 9.496 | 9.276 | 1.1 | 13.122 | 13.39 | 1.1
1.828 | 1.654 | 1.2 | 3.24 | 2.958 | 1.2 | 8.1158 | 5.322 | 1.2 | 8.766 | 8.484 | 1.2 | 10.652 | 10.232 | 1.2 | 14.254 | 14.44 | 1.2
1.932 | 1.736 | 1.3 | 3.43 | 3.132 | 1.3 | 9.1472 | 5.698 | 1.3 | 9.514 | 9.146 | 1.3 | 11.808 | 11.188 | 1.3 | 15.386 | 15.49 | 1.3
2.036 | 1.818 | 1.4 | 3.62 | 3.306 | 1.4 | 10.1786 | 6.074 | 1.4 | 10.262 | 9.808 | 1.4 | 12.964 | 12.144 | 1.4 | 16.518 | 16.54 | 1.4
2.14 | 1.9 | 1.5 | 3.81 | 3.48 | 1.5 | 11.21 | 6.45 | 1.5 | 11.01 | 10.47 | 1.5 | 14.12 | 13.1 | 1.5 | 17.65 | 17.59 | 1.5
2.242 | 1.974 | 1.6 | 4.002 | 3.622 | 1.6 | 12.142 | 6.682 | 1.6 | 11.54 | 10.968 | 1.6 | 15.03 | 13.736 | 1.6 | 18.668 | 18.498 | 1.6
2.344 | 2.048 | 1.7 | 4.194 | 3.764 | 1.7 | 13.074 | 6.914 | 1.7 | 12.07 | 11.466 | 1.7 | 15.94 | 14.372 | 1.7 | 19.686 | 19.406 | 1.7
2.446 | 2.122 | 1.8 | 4.386 | 3.906 | 1.8 | 14.006 | 7.146 | 1.8 | 12.6 | 11.964 | 1.8 | 16.85 | 15.008 | 1.8 | 20.704 | 20.314 | 1.8
2.548 | 2.196 | 1.9 | 4.578 | 4.048 | 1.9 | 14.938 | 7.378 | 1.9 | 13.13 | 12.462 | 1.9 | 17.76 | 15.644 | 1.9 | 21.722 | 21.222 | 1.9
2.65 | 2.27 | 2 | 4.77 | 4.19 | 2 | 15.87 | 7.61 | 2 | 13.66 | 12.96 | 2 | 18.67 | 16.28 | 2 | 22.74 | 22.13 | 2
2.698 | 2.316 | 2.1 | 4.92 | 4.324 | 2.1 | 16.838 | 7.828 | 2.1 | 14.132 | 13.416 | 2.1 | 19.542 | 16.87 | 2.1 | 23.766 | 22.834 | 2.1
2.746 | 2.362 | 2.2 | 5.07 | 4.458 | 2.2 | 17.806 | 8.046 | 2.2 | 14.604 | 13.872 | 2.2 | 20.414 | 17.46 | 2.2 | 24.792 | 23.538 | 2.2
2.794 | 2.408 | 2.3 | 5.22 | 4.592 | 2.3 | 18.774 | 8.264 | 2.3 | 15.076 | 14.328 | 2.3 | 21.286 | 18.05 | 2.3 | 25.818 | 24.242 | 2.3
2.842 | 2.454 | 2.4 | 5.37 | 4.726 | 2.4 | 19.742 | 8.482 | 2.4 | 15.548 | 14.784 | 2.4 | 22.158 | 18.64 | 2.4 | 26.844 | 24.946 | 2.4
2.89 | 2.5 | 2.5 | 5.52 | 4.86 | 2.5 | 20.71 | 8.7 | 2.5 | 16.02 | 15.24 | 2.5 | 23.03 | 19.23 | 2.5 | 27.87 | 25.65 | 2.5
3.116 | 2.578 | 2.6 | 5.716 | 4.986 | 2.6 | 21.566 | 8.84 | 2.6 | 16.458 | 15.646 | 2.6 | 23.812 | 19.722 | 2.6 | 28.76 | 26.412 | 2.6
3.342 | 2.656 | 2.7 | 5.912 | 5.112 | 2.7 | 22.422 | 8.98 | 2.7 | 16.896 | 16.052 | 2.7 | 24.594 | 20.214 | 2.7 | 29.65 | 27.174 | 2.7
3.568 | 2.734 | 2.8 | 6.108 | 5.238 | 2.8 | 23.278 | 9.12 | 2.8 | 17.334 | 16.458 | 2.8 | 25.376 | 20.706 | 2.8 | 30.54 | 27.936 | 2.8
3.794 | 2.812 | 2.9 | 6.304 | 5.364 | 2.9 | 24.134 | 9.26 | 2.9 | 17.772 | 16.864 | 2.9 | 26.158 | 21.198 | 2.9 | 31.43 | 28.698 | 2.9
4.02 | 2.89 | 3 | 6.5 | 5.49 | 3 | 24.99 | 9.4 | 3 | 18.21 | 17.27 | 3 | 26.94 | 21.69 | 3 | 32.32 | 29.46 | 3
4.288 | 2.952 | 3.1 | 6.772 | 5.61 | 3.1 | 26.194 | 9.544 | 3.1 | 18.718 | 17.682 | 3.1 | 28.148 | 22.166 | 3.1 | 33.332 | 30.194 | 3.1
4.556 | 3.014 | 3.2 | 7.044 | 5.73 | 3.2 | 27.398 | 9.688 | 3.2 | 19.226 | 18.094 | 3.2 | 29.356 | 22.642 | 3.2 | 34.344 | 30.928 | 3.2
4.824 | 3.076 | 3.3 | 7.316 | 5.85 | 3.3 | 28.602 | 9.832 | 3.3 | 19.734 | 18.506 | 3.3 | 30.564 | 23.118 | 3.3 | 35.356 | 31.662 | 3.3
5.092 | 3.138 | 3.4 | 7.588 | 5.97 | 3.4 | 29.806 | 9.976 | 3.4 | 20.242 | 18.918 | 3.4 | 31.772 | 23.594 | 3.4 | 36.368 | 32.396 | 3.4
5.36 | 3.2 | 3.5 | 7.86 | 6.09 | 3.5 | 31.01 | 10.12 | 3.5 | 20.75 | 19.33 | 3.5 | 32.98 | 24.07 | 3.5 | 37.38 | 33.13 | 3.5
5.648 | 3.258 | 3.6 | 8.264 | 6.172 | 3.6 | 31.166 | 10.196 | 3.6 | 21.202 | 19.664 | 3.6 | 34.374 | 24.456 | 3.6 | 38.444 | 33.768 | 3.6
5.936 | 3.316 | 3.7 | 8.668 | 6.254 | 3.7 | 31.322 | 10.272 | 3.7 | 21.654 | 19.998 | 3.7 | 35.768 | 24.842 | 3.7 | 39.508 | 34.406 | 3.7
6.224 | 3.374 | 3.8 | 9.072 | 6.336 | 3.8 | 31.478 | 10.348 | 3.8 | 22.106 | 20.332 | 3.8 | 37.162 | 25.228 | 3.8 | 40.572 | 35.044 | 3.8
6.512 | 3.432 | 3.9 | 9.476 | 6.418 | 3.9 | 31.634 | 10.424 | 3.9 | 22.558 | 20.666 | 3.9 | 38.556 | 25.614 | 3.9 | 41.636 | 35.682 | 3.9
6.8 | 3.49 | 4 | 9.88 | 6.5 | 4 | 31.79 | 10.5 | 4 | 23.01 | 21 | 4 | 39.95 | 26 | 4 | 42.7 | 36.32 | 4
[15 empty] | 44.1 | 37.056 | 4.1
[15 empty] | 45.5 | 37.792 | 4.2
[15 empty] | 46.9 | 38.528 | 4.3
[15 empty] | 48.3 | 39.264 | 4.4
[15 empty] | 49.7 | 40 | 4.5

## Frese VODRV flanged 2024
QUICK - CALC Frese STBV, VODRV Flanged
Setting & Selection program
Input
Input Q: |  | 100 | (m3/h) Flow
Measured diff. Pressure |  | 10 | (kPa) Total valve
Kv: (Required) |  | 316.2278
DN | KV (Fully open valve) |  | Pre-set
65 | 94.6 |  | NOT POSSIBLE
80 | 119 |  | NOT POSSIBLE
100 | 215 |  | NOT POSSIBLE
125 | 289 |  | NOT POSSIBLE
150 | 403 |  | 7.4
200 | 852 |  | 4.5
250 | 1240 |  | 4.1
300 | 1420 |  | 4.7
350 | 2085 |  | 2.1
400 | 2189 |  | 1.5
450 | 2526 |  | 1.4
500 | 3381 |  | 0.9
Dimension
DN65 | DN80 | DN100 | DN125 | DN150 | DN200 | DN250 | DN300 | DN350 | DN400 | DN450 | DN500 | Preset
KV | KV | KV | KV | KV | KV | KV | KV | KV | KV | KV | KV
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.3 | 0.57 | 0.9 | 0.97 | 1.41 | 4.84 | 6.99 | 9.36 | 16.8991 | 23.2404 | 25.4536 | 32.1578 | 0.1
0.6 | 1.14 | 1.8 | 1.94 | 2.82 | 9.68 | 13.98 | 18.72 | 33.7981 | 46.4808 | 50.9073 | 64.3155 | 0.2
0.9 | 1.71 | 2.7 | 2.91 | 4.23 | 14.52 | 20.97 | 28.08 | 50.6972 | 69.7212 | 76.3609 | 96.4733 | 0.3
1.2 | 2.28 | 3.6 | 3.88 | 5.64 | 19.36 | 27.96 | 37.44 | 67.5963 | 92.9616 | 101.8145 | 128.6311 | 0.4
1.5 | 2.85 | 4.5 | 4.85 | 7.05 | 24.2 | 34.95 | 46.8 | 84.4954 | 116.202 | 127.2681 | 160.7888 | 0.5
1.8 | 3.42 | 5.4 | 5.82 | 8.46 | 29.04 | 41.94 | 49.06 | 101.3944 | 139.4424 | 152.7218 | 192.9466 | 0.6
2.1 | 3.99 | 6.3 | 6.79 | 9.87 | 33.88 | 48.93 | 51.32 | 118.2935 | 162.6828 | 178.1754 | 225.1044 | 0.7
2.4 | 4.56 | 7.2 | 7.76 | 11.28 | 38.72 | 55.92 | 53.58 | 135.1926 | 185.9232 | 203.629 | 257.2621 | 0.8
2.7 | 5.13 | 8.1 | 8.73 | 12.69 | 43.56 | 62.91 | 55.84 | 152.0916 | 209.1636 | 229.0826 | 289.4199 | 0.9
3 | 5.7 | 9 | 9.7 | 14.1 | 48.4 | 69.9 | 58.1 | 168.9907 | 232.404 | 254.5363 | 321.5777 | 1
3.62 | 6.14 | 10.28 | 10.92 | 16.99 | 54.96 | 78.41 | 65.99 | 181.8949 | 247.5387 | 269.2989 | 345.9495 | 1.1
4.24 | 6.58 | 11.56 | 12.14 | 19.88 | 61.52 | 86.92 | 73.88 | 194.7992 | 262.6734 | 284.0616 | 370.3214 | 1.2
4.86 | 7.02 | 12.84 | 13.36 | 22.77 | 68.08 | 95.43 | 81.77 | 207.7034 | 277.8082 | 298.8242 | 394.6933 | 1.3
5.48 | 7.46 | 14.12 | 14.58 | 25.66 | 74.64 | 103.94 | 89.66 | 220.6076 | 292.9429 | 313.5869 | 419.0652 | 1.4
6.1 | 7.9 | 15.4 | 15.8 | 28.55 | 81.2 | 112.45 | 97.55 | 233.5119 | 308.0776 | 328.3495 | 443.437 | 1.5
6.72 | 8.34 | 16.68 | 17.02 | 31.44 | 87.76 | 120.96 | 105.44 | 246.4161 | 323.2123 | 343.1122 | 467.8089 | 1.6
7.34 | 8.78 | 17.96 | 18.24 | 34.33 | 94.32 | 129.47 | 113.33 | 259.3203 | 338.347 | 357.8749 | 492.1808 | 1.7
7.96 | 9.22 | 19.24 | 19.46 | 37.22 | 100.88 | 137.98 | 121.22 | 272.2246 | 353.4817 | 372.6375 | 516.5527 | 1.8
8.58 | 9.66 | 20.52 | 20.68 | 40.11 | 107.44 | 146.49 | 129.11 | 285.1288 | 368.6165 | 387.4002 | 540.9245 | 1.9
9.2 | 10.1 | 21.8 | 21.9 | 43 | 114 | 155 | 137 | 298.033 | 383.7512 | 402.1628 | 565.2964 | 2
10.17 | 10.77 | 24.15 | 24.99 | 48 | 119 | 163.9 | 144.9 | 311.5089 | 398.0993 | 418.4651 | 587.152 | 2.1
11.14 | 11.44 | 26.5 | 28.08 | 53 | 124 | 172.8 | 152.8 | 324.9848 | 412.4474 | 434.7673 | 609.0076 | 2.2
12.11 | 12.11 | 28.85 | 31.17 | 58 | 129 | 181.7 | 160.7 | 338.4607 | 426.7956 | 451.0696 | 630.8633 | 2.3
13.08 | 12.78 | 31.2 | 34.26 | 63 | 134 | 190.6 | 168.6 | 351.9366 | 441.1437 | 467.3719 | 652.7189 | 2.4
14.05 | 13.45 | 33.55 | 37.35 | 68 | 139 | 199.5 | 176.5 | 365.4125 | 455.4918 | 483.6741 | 674.5745 | 2.5
15.02 | 14.12 | 35.9 | 40.44 | 73 | 144 | 208.4 | 184.4 | 378.8884 | 469.8399 | 499.9764 | 696.4301 | 2.6
15.99 | 14.79 | 38.25 | 43.53 | 78 | 149 | 217.3 | 192.3 | 392.3643 | 484.1881 | 516.2786 | 718.2858 | 2.7
16.96 | 15.46 | 40.6 | 46.62 | 83 | 154 | 226.2 | 200.2 | 405.8402 | 498.5362 | 532.5809 | 740.1414 | 2.8
17.93 | 16.13 | 42.95 | 49.71 | 88 | 159 | 235.1 | 208.1 | 419.3161 | 512.8843 | 548.8832 | 761.997 | 2.9
18.9 | 16.8 | 45.3 | 52.8 | 93 | 164 | 244 | 216 | 432.792 | 527.2324 | 565.1854 | 783.8526 | 3
21.06 | 18.63 | 48.09 | 57.44 | 98.3 | 171.4 | 249.5 | 221.8 | 444.7623 | 541.2176 | 581.867 | 804.5787 | 3.1
23.22 | 20.46 | 50.88 | 62.08 | 103.6 | 178.8 | 255 | 227.6 | 456.7326 | 555.2027 | 598.5486 | 825.3048 | 3.2
25.38 | 22.29 | 53.67 | 66.72 | 108.9 | 186.2 | 260.5 | 233.4 | 468.7028 | 569.1879 | 615.2301 | 846.0308 | 3.3
27.54 | 24.12 | 56.46 | 71.36 | 114.2 | 193.6 | 266 | 239.2 | 480.6731 | 583.173 | 631.9117 | 866.7569 | 3.4
29.7 | 25.95 | 59.25 | 76 | 119.5 | 201 | 271.5 | 245 | 492.6434 | 597.1582 | 648.5933 | 887.483 | 3.5
31.86 | 27.78 | 62.04 | 80.64 | 124.8 | 208.4 | 277 | 250.8 | 504.6136 | 611.1433 | 665.2748 | 908.209 | 3.6
34.02 | 29.61 | 64.83 | 85.28 | 130.1 | 215.8 | 282.5 | 256.6 | 516.5839 | 625.1285 | 681.9564 | 928.9351 | 3.7
36.18 | 31.44 | 67.62 | 89.92 | 135.4 | 223.2 | 288 | 262.4 | 528.5542 | 639.1136 | 698.638 | 949.6612 | 3.8
38.34 | 33.27 | 70.41 | 94.56 | 140.7 | 230.6 | 293.5 | 268.2 | 540.5244 | 653.0987 | 715.3195 | 970.3872 | 3.9
40.5 | 35.1 | 73.2 | 99.2 | 146 | 238 | 299 | 274 | 552.4947 | 667.0839 | 732.0011 | 991.1133 | 4
42.61 | 37.94 | 77.56 | 105.47 | 151.7 | 253.4 | 310.5 | 279.5 | 565.0749 | 680.1528 | 746.04 | 1010.831 | 4.1
44.72 | 40.78 | 81.92 | 111.74 | 157.4 | 268.8 | 322 | 285 | 577.655 | 693.2217 | 760.0789 | 1030.5486 | 4.2
46.83 | 43.62 | 86.28 | 118.01 | 163.1 | 284.2 | 333.5 | 290.5 | 590.2351 | 706.2906 | 774.1178 | 1050.2663 | 4.3
48.94 | 46.46 | 90.64 | 124.28 | 168.8 | 299.6 | 345 | 296 | 602.8153 | 719.3594 | 788.1568 | 1069.9839 | 4.4
51.05 | 49.3 | 95 | 130.55 | 174.5 | 315 | 356.5 | 301.5 | 615.3954 | 732.4283 | 802.1957 | 1089.7016 | 4.5
53.16 | 52.14 | 99.36 | 136.82 | 180.2 | 330.4 | 368 | 307 | 627.9756 | 745.4972 | 816.2346 | 1109.4193 | 4.6
55.27 | 54.98 | 103.72 | 143.09 | 185.9 | 345.8 | 379.5 | 312.5 | 640.5557 | 758.5661 | 830.2735 | 1129.1369 | 4.7
57.38 | 57.82 | 108.08 | 149.36 | 191.6 | 361.2 | 391 | 318 | 653.1359 | 771.635 | 844.3124 | 1148.8546 | 4.8
59.49 | 60.66 | 112.44 | 155.63 | 197.3 | 376.6 | 402.5 | 323.5 | 665.716 | 784.7039 | 858.3513 | 1168.5723 | 4.9
61.6 | 63.5 | 116.8 | 161.9 | 203 | 392 | 414 | 329 | 678.2962 | 797.7728 | 872.3902 | 1188.2899 | 5
62.96 | 65.71 | 120.32 | 165.2 | 206.3 | 403.5 | 426.7 | 344.4 | 688.2255 | 808.4162 | 887.4938 | 1206.1978 | 5.1
64.32 | 67.92 | 123.84 | 168.5 | 209.6 | 415 | 439.4 | 359.8 | 698.1548 | 819.0596 | 902.5975 | 1224.1056 | 5.2
65.68 | 70.13 | 127.36 | 171.8 | 212.9 | 426.5 | 452.1 | 375.2 | 708.0841 | 829.703 | 917.7011 | 1242.0135 | 5.3
67.04 | 72.34 | 130.88 | 175.1 | 216.2 | 438 | 464.8 | 390.6 | 718.0134 | 840.3464 | 932.8047 | 1259.9213 | 5.4
68.4 | 74.55 | 134.4 | 178.4 | 219.5 | 449.5 | 477.5 | 406 | 727.9427 | 850.9898 | 947.9083 | 1277.8292 | 5.5
69.76 | 76.76 | 137.92 | 181.7 | 222.8 | 461 | 490.2 | 421.4 | 737.872 | 861.6332 | 963.012 | 1295.737 | 5.6
71.12 | 78.97 | 141.44 | 185 | 226.1 | 472.5 | 502.9 | 436.8 | 747.8013 | 872.2766 | 978.1156 | 1313.6448 | 5.7
72.48 | 81.18 | 144.96 | 188.3 | 229.4 | 484 | 515.6 | 452.2 | 757.7306 | 882.92 | 993.2192 | 1331.5527 | 5.8
73.84 | 83.39 | 148.48 | 191.6 | 232.7 | 495.5 | 528.3 | 467.6 | 767.6599 | 893.5633 | 1008.3228 | 1349.4605 | 5.9
75.2 | 85.6 | 152 | 194.9 | 236 | 507 | 541 | 483 | 777.5892 | 904.2067 | 1023.4265 | 1367.3684 | 6
76.09 | 87.03 | 154.73 | 198.51 | 241.6 | 516.7 | 553.2 | 496.3 | 786.8066 | 913.4261 | 1035.2657 | 1380.8412 | 6.1
76.98 | 88.46 | 157.46 | 202.12 | 247.2 | 526.4 | 565.4 | 509.6 | 796.024 | 922.6455 | 1047.105 | 1394.314 | 6.2
77.87 | 89.89 | 160.19 | 205.73 | 252.8 | 536.1 | 577.6 | 522.9 | 805.2414 | 931.8648 | 1058.9443 | 1407.7869 | 6.3
78.76 | 91.32 | 162.92 | 209.34 | 258.4 | 545.8 | 589.8 | 536.2 | 814.4588 | 941.0842 | 1070.7836 | 1421.2597 | 6.4
79.65 | 92.75 | 165.65 | 212.95 | 264 | 555.5 | 602 | 549.5 | 823.6762 | 950.3036 | 1082.6229 | 1434.7325 | 6.5
80.54 | 94.18 | 168.38 | 216.56 | 269.6 | 565.2 | 614.2 | 562.8 | 832.8936 | 959.5229 | 1094.4622 | 1448.2053 | 6.6
81.43 | 95.61 | 171.11 | 220.17 | 275.2 | 574.9 | 626.4 | 576.1 | 842.111 | 968.7423 | 1106.3014 | 1461.6781 | 6.7
82.32 | 97.04 | 173.84 | 223.78 | 280.8 | 584.6 | 638.6 | 589.4 | 851.3284 | 977.9616 | 1118.1407 | 1475.151 | 6.8
83.21 | 98.47 | 176.57 | 227.39 | 286.4 | 594.3 | 650.8 | 602.7 | 860.5458 | 987.181 | 1129.98 | 1488.6238 | 6.9
84.1 | 99.9 | 179.3 | 231 | 292 | 604 | 663 | 616 | 869.7632 | 996.4004 | 1141.8193 | 1502.0966 | 7
84.76 | 100.85 | 181.66 | 233.86 | 297.8 | 612.6 | 675.3 | 629.6 | 878.1781 | 1004.7412 | 1155.5018 | 1512.7934 | 7.1
85.42 | 101.8 | 184.02 | 236.72 | 303.6 | 621.2 | 687.6 | 643.2 | 886.5931 | 1013.0821 | 1169.1844 | 1523.4903 | 7.2
86.08 | 102.75 | 186.38 | 239.58 | 309.4 | 629.8 | 699.9 | 656.8 | 895.008 | 1021.423 | 1182.8669 | 1534.1871 | 7.3
86.74 | 103.7 | 188.74 | 242.44 | 315.2 | 638.4 | 712.2 | 670.4 | 903.4229 | 1029.7639 | 1196.5495 | 1544.8839 | 7.4
87.4 | 104.65 | 191.1 | 245.3 | 321 | 647 | 724.5 | 684 | 911.8379 | 1038.1047 | 1210.2321 | 1555.5807 | 7.5
88.06 | 105.6 | 193.46 | 248.16 | 326.8 | 655.6 | 736.8 | 697.6 | 920.2528 | 1046.4456 | 1223.9146 | 1566.2776 | 7.6
88.72 | 106.55 | 195.82 | 251.02 | 332.6 | 664.2 | 749.1 | 711.2 | 928.6678 | 1054.7865 | 1237.5972 | 1576.9744 | 7.7
89.38 | 107.5 | 198.18 | 253.88 | 338.4 | 672.8 | 761.4 | 724.8 | 937.0827 | 1063.1274 | 1251.2797 | 1587.6712 | 7.8
90.04 | 108.45 | 200.54 | 256.74 | 344.2 | 681.4 | 773.7 | 738.4 | 945.4976 | 1071.4682 | 1264.9623 | 1598.368 | 7.9
90.7 | 109.4 | 202.9 | 259.6 | 350 | 690 | 786 | 752 | 953.9126 | 1079.8091 | 1278.6448 | 1609.0649 | 8
91.09 | 110.36 | 204.11 | 262.54 | 355.3 | 699.3 | 799.1 | 765.3 | 959.0791 | 1083.8874 | 1284.3629 | 1618.2765 | 8.1
91.48 | 111.32 | 205.32 | 265.48 | 360.6 | 708.6 | 812.2 | 778.6 | 964.2455 | 1087.9657 | 1290.081 | 1627.4881 | 8.2
91.87 | 112.28 | 206.53 | 268.42 | 365.9 | 717.9 | 825.3 | 791.9 | 969.412 | 1092.044 | 1295.7991 | 1636.6997 | 8.3
92.26 | 113.24 | 207.74 | 271.36 | 371.2 | 727.2 | 838.4 | 805.2 | 974.5785 | 1096.1223 | 1301.5172 | 1645.9113 | 8.4
92.65 | 114.2 | 208.95 | 274.3 | 376.5 | 736.5 | 851.5 | 818.5 | 979.7449 | 1100.2006 | 1307.2353 | 1655.1229 | 8.5
93.04 | 115.16 | 210.16 | 277.24 | 381.8 | 745.8 | 864.6 | 831.8 | 984.9114 | 1104.2789 | 1312.9533 | 1664.3345 | 8.6
93.43 | 116.12 | 211.37 | 280.18 | 387.1 | 755.1 | 877.7 | 845.1 | 990.0779 | 1108.3572 | 1318.6714 | 1673.5461 | 8.7
93.82 | 117.08 | 212.58 | 283.12 | 392.4 | 764.4 | 890.8 | 858.4 | 995.2444 | 1112.4355 | 1324.3895 | 1682.7577 | 8.8
94.21 | 118.04 | 213.79 | 286.06 | 397.7 | 773.7 | 903.9 | 871.7 | 1000.4108 | 1116.5138 | 1330.1076 | 1691.9693 | 8.9
94.6 | 119 | 215 | 289 | 403 | 783 | 917 | 885 | 1005.5773 | 1120.5921 | 1335.8257 | 1701.1809 | 9
[5 empty] | 789.9 | 928.3 | 899.5 | 1007.8488 | 1122.9188 | 1346.502 | 1706.3701 | 9.1
[5 empty] | 796.8 | 939.6 | 914 | 1010.1202 | 1125.2455 | 1357.1783 | 1711.5593 | 9.2
[5 empty] | 803.7 | 950.9 | 928.5 | 1012.3917 | 1127.5722 | 1367.8546 | 1716.7485 | 9.3
[5 empty] | 810.6 | 962.2 | 943 | 1014.6631 | 1129.8989 | 1378.531 | 1721.9377 | 9.4
[5 empty] | 817 | 973.5 | 957.5 | 1016.9346 | 1132.2256 | 1389.2073 | 1727.1269 | 9.5
[5 empty] | 824.4 | 984.8 | 972 | 1019.206 | 1134.5523 | 1399.8836 | 1732.3161 | 9.6
[5 empty] | 831.3 | 996.1 | 986.5 | 1021.4775 | 1136.879 | 1410.5599 | 1737.5053 | 9.7
[5 empty] | 838.2 | 1007.4 | 1001 | 1023.7489 | 1139.2057 | 1421.2363 | 1742.6945 | 9.8
[5 empty] | 845.1 | 1018.7 | 1015.5 | 1026.0204 | 1141.5324 | 1431.9126 | 1747.8837 | 9.9
[5 empty] | 852 | 1030 | 1030 | 1028.2918 | 1143.8591 | 1442.5889 | 1753.0729 | 10
[6 empty] | 1041 | 1043 | 1037.7459 | 1146.9471 | 1454.0802 | 1756.6543 | 10.1
[6 empty] | 1052 | 1056 | 1047.2 | 1150.0352 | 1465.5714 | 1760.2358 | 10.2
[6 empty] | 1063 | 1069 | 1056.654 | 1153.1232 | 1477.0627 | 1763.8172 | 10.3
[6 empty] | 1074 | 1082 | 1066.1081 | 1156.2113 | 1488.554 | 1767.3986 | 10.4
[6 empty] | 1085 | 1095 | 1075.5622 | 1159.2993 | 1500.0452 | 1770.98 | 10.5
[6 empty] | 1096 | 1108 | 1085.0162 | 1162.3873 | 1511.5365 | 1774.5615 | 10.6
[6 empty] | 1107 | 1121 | 1094.4703 | 1165.4754 | 1523.0277 | 1778.1429 | 10.7
[6 empty] | 1118 | 1134 | 1103.9243 | 1168.5634 | 1534.519 | 1781.7243 | 10.8
[6 empty] | 1129 | 1147 | 1113.3784 | 1171.6514 | 1546.0103 | 1785.3057 | 10.9
[6 empty] | 1140 | 1160 | 1122.8325 | 1174.7395 | 1557.5015 | 1788.8871 | 11
[6 empty] | 1150 | 1173 | 1136.1469 | 1184.2658 | 1559.6441 | 1802.1741 | 11.1
[6 empty] | 1160 | 1186 | 1149.4613 | 1193.7922 | 1561.7868 | 1815.461 | 11.2
[6 empty] | 1170 | 1199 | 1162.7757 | 1203.3185 | 1563.9294 | 1828.748 | 11.3
[6 empty] | 1180 | 1212 | 1176.0901 | 1212.8448 | 1566.072 | 1842.0349 | 11.4
[6 empty] | 1190 | 1225 | 1189.4045 | 1222.3712 | 1568.2146 | 1855.3219 | 11.5
[6 empty] | 1200 | 1238 | 1202.7189 | 1231.8975 | 1570.3572 | 1868.6088 | 11.6
[6 empty] | 1210 | 1251 | 1216.0333 | 1241.4239 | 1572.4998 | 1881.8958 | 11.7
[6 empty] | 1220 | 1264 | 1229.3477 | 1250.9502 | 1574.6424 | 1895.1827 | 11.8
[6 empty] | 1230 | 1277 | 1242.6621 | 1260.4766 | 1576.785 | 1908.4697 | 11.9
[6 empty] | 1240 | 1290 | 1255.9765 | 1270.0029 | 1578.9277 | 1921.7566 | 12
[7 empty] | 1303 | 1267.2721 | 1283.2481 | 1580.2658 | 1941.1449 | 12.1
[7 empty] | 1316 | 1278.5677 | 1296.4934 | 1581.604 | 1960.5332 | 12.2
[7 empty] | 1329 | 1289.8632 | 1309.7386 | 1582.9422 | 1979.9216 | 12.3
[7 empty] | 1342 | 1301.1588 | 1322.9838 | 1584.2804 | 1999.3099 | 12.4
[7 empty] | 1355 | 1312.4543 | 1336.229 | 1585.6186 | 2018.6982 | 12.5
[7 empty] | 1368 | 1323.7499 | 1349.4742 | 1586.9568 | 2038.0865 | 12.6
[7 empty] | 1381 | 1335.0454 | 1362.7195 | 1588.295 | 2057.4749 | 12.7
[7 empty] | 1394 | 1346.341 | 1375.9647 | 1589.6332 | 2076.8632 | 12.8
[7 empty] | 1407 | 1357.6365 | 1389.2099 | 1590.9714 | 2096.2515 | 12.9
[7 empty] | 1420 | 1368.9321 | 1402.4551 | 1592.3095 | 2115.6398 | 13
[8 empty] | 1376.847 | 1415.4352 | 1606.5187 | 2134.6828 | 13.1
[8 empty] | 1384.7619 | 1428.4153 | 1620.7279 | 2153.7257 | 13.2
[8 empty] | 1392.6768 | 1441.3954 | 1634.9371 | 2172.7686 | 13.3
[8 empty] | 1400.5917 | 1454.3755 | 1649.1463 | 2191.8116 | 13.4
[8 empty] | 1408.5066 | 1467.3556 | 1663.3555 | 2210.8545 | 13.5
[8 empty] | 1416.4215 | 1480.3357 | 1677.5647 | 2229.8975 | 13.6
[8 empty] | 1424.3363 | 1493.3158 | 1691.7739 | 2248.9404 | 13.7
[8 empty] | 1432.2512 | 1506.2959 | 1705.9831 | 2267.9833 | 13.8
[8 empty] | 1440.1661 | 1519.276 | 1720.1923 | 2287.0263 | 13.9
[8 empty] | 1448.081 | 1532.2561 | 1734.4015 | 2306.0692 | 14
[8 empty] | 1460.338 | 1545.6621 | 1741.3878 | 2325.8085 | 14.1
[8 empty] | 1472.595 | 1559.0682 | 1748.374 | 2345.5479 | 14.2
[8 empty] | 1484.8521 | 1572.4742 | 1755.3602 | 2365.2872 | 14.3
[8 empty] | 1497.1091 | 1585.8802 | 1762.3464 | 2385.0265 | 14.4
[8 empty] | 1509.3661 | 1599.2863 | 1769.3327 | 2404.7659 | 14.5
[8 empty] | 1521.6231 | 1612.6923 | 1776.3189 | 2424.5052 | 14.6
[8 empty] | 1533.8801 | 1626.0983 | 1783.3051 | 2444.2445 | 14.7
[8 empty] | 1546.1371 | 1639.5044 | 1790.2913 | 2463.9839 | 14.8
[8 empty] | 1558.3941 | 1652.9104 | 1797.2776 | 2483.7232 | 14.9
[8 empty] | 1570.6511 | 1666.3164 | 1804.2638 | 2503.4625 | 15
[8 empty] | 1583.2076 | 1678.5452 | 1820.7239 | 2525.4659 | 15.1
[8 empty] | 1595.764 | 1690.7739 | 1837.1841 | 2547.4694 | 15.2
[8 empty] | 1608.3204 | 1703.0027 | 1853.6442 | 2569.4728 | 15.3
[8 empty] | 1620.8769 | 1715.2314 | 1870.1044 | 2591.4762 | 15.4
[8 empty] | 1633.4333 | 1727.4602 | 1886.5645 | 2613.4796 | 15.5
[8 empty] | 1645.9897 | 1739.689 | 1903.0246 | 2635.483 | 15.6
[8 empty] | 1658.5462 | 1751.9177 | 1919.4848 | 2657.4864 | 15.7
[8 empty] | 1671.1026 | 1764.1465 | 1935.9449 | 2679.4899 | 15.8
[8 empty] | 1683.659 | 1776.3752 | 1952.4051 | 2701.4933 | 15.9
[8 empty] | 1696.2155 | 1788.604 | 1968.8652 | 2723.4967 | 16
[8 empty] | 1709.8092 | 1803.3003 | 1985.9806 | 2743.528 | 16.1
[8 empty] | 1723.403 | 1817.9967 | 2003.096 | 2763.5593 | 16.2
[8 empty] | 1736.9967 | 1832.6931 | 2020.2114 | 2783.5907 | 16.3
[8 empty] | 1750.5905 | 1847.3894 | 2037.3268 | 2803.622 | 16.4
[8 empty] | 1764.1842 | 1862.0858 | 2054.4422 | 2823.6533 | 16.5
[8 empty] | 1777.778 | 1876.7822 | 2071.5576 | 2843.6847 | 16.6
[8 empty] | 1791.3717 | 1891.4785 | 2088.673 | 2863.716 | 16.7
[8 empty] | 1804.9655 | 1906.1749 | 2105.7884 | 2883.7473 | 16.8
[8 empty] | 1818.5593 | 1920.8712 | 2122.9038 | 2903.7786 | 16.9
[8 empty] | 1832.153 | 1935.5676 | 2140.0192 | 2923.81 | 17
[8 empty] | 1842.4906 | 1951.0868 | 2158.2217 | 2945.2512 | 17.1
[8 empty] | 1852.8283 | 1966.6061 | 2176.4243 | 2966.6924 | 17.2
[8 empty] | 1863.1659 | 1982.1253 | 2194.6268 | 2988.1336 | 17.3
[8 empty] | 1873.5035 | 1997.6446 | 2212.8294 | 3009.5748 | 17.4
[8 empty] | 1883.8411 | 2013.1638 | 2231.0319 | 3031.016 | 17.5
[8 empty] | 1894.1787 | 2028.6831 | 2249.2345 | 3052.4572 | 17.6
[8 empty] | 1904.5164 | 2044.2023 | 2267.4371 | 3073.8984 | 17.7
[8 empty] | 1914.854 | 2059.7216 | 2285.6396 | 3095.3396 | 17.8
[8 empty] | 1925.1916 | 2075.2408 | 2303.8422 | 3116.7809 | 17.9
[8 empty] | 1935.5292 | 2090.76 | 2322.0447 | 3138.2221 | 18
[8 empty] | 1950.4763 | 2100.584 | 2342.4402 | 3162.4999 | 18.1
[8 empty] | 1965.4234 | 2110.408 | 2362.8358 | 3186.7777 | 18.2
[8 empty] | 1980.3705 | 2120.232 | 2383.2313 | 3211.0554 | 18.3
[8 empty] | 1995.3175 | 2130.056 | 2403.6268 | 3235.3332 | 18.4
[8 empty] | 2010.2646 | 2139.88 | 2424.0224 | 3259.611 | 18.5
[8 empty] | 2025.2117 | 2149.704 | 2444.4179 | 3283.8888 | 18.6
[8 empty] | 2040.1588 | 2159.528 | 2464.8134 | 3308.1666 | 18.7
[8 empty] | 2055.1058 | 2169.352 | 2485.2089 | 3332.4444 | 18.8
[8 empty] | 2070.0529 | 2179.176 | 2505.6045 | 3356.7222 | 18.9
[8 empty] | 2085 | 2189 | 2526 | 3381 | 19

## OPTIMA Compact Veriflow FCP
QUICK - CONTROL OPTIMA Compact Veriflow
Flow Commissioning program
Input
∆P measured = | 15 | kPa (PT plug in position Q)
Pre-set = | 4
Dimension | Range |  | Verification
| Flow (l/h) |  | Flow (l/h)
DN10 Low 2,5 | 30-200 |  | 195.973
DN10 Low 5,0 | 65-370 |  | 324.9433
DN15 Low 2,5 | 30-200 |  | 195.973
DN15 Low 5,0 | 65-370 |  | 324.9433
DN15 High 2,5 | 100-575 |  | 557.7096
DN15 High 5,0 | 220-1330 |  | 1281.9575
DN15 High 5,5 | 300-1800 |  | 1471.7337
DN20 High 2,5 | 100-575 |  | 557.7096
DN20 High 5,0 | 220-1330 |  | 1281.9575
DN20 High 5,5 | 300-1800 |  | 1471.7337
DN25 Low 5,5 | 280-1800 |  | 1471.7337
DN25L High 5,5 | 600-3609 |  | 3110.0056
DN32 | 550-4001 |  | 3253.306
DN40 | 1370-9500 |  | 9333.8899
DN50 | 1400-11500 |  | 8559.2932
Veriflow Low 2,5 DN10/15 |  | Veriflow Low 5,0 DN10/15 |  | Veriflow High 2,5 DN15/20 |  | Veriflow High 5,0 DN15/20 |  | Veriflow High 5,5 DN15/20 |  | Veriflow Low 5,5 DN25
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
0.5 | 0.121
0.6 | 0.124 | 0.6 | 0.134 | 0.6 | 0.25 | 0.6 | 0.595 | 0.6 | 0.675 | 0.6 | 0.647
0.8 | 0.136 | 0.8 | 0.184 | 0.8 | 0.314 | 0.8 | 0.755 | 0.8 | 0.849 | 0.8 | 0.77
1 | 0.153 | 1 | 0.231 | 1 | 0.378 | 1 | 0.913 | 1 | 1.03 | 1 | 0.916
1.2 | 0.174 | 1.2 | 0.275 | 1.2 | 0.442 | 1.2 | 1.07 | 1.2 | 1.22 | 1.2 | 1.08
1.4 | 0.198 | 1.4 | 0.317 | 1.4 | 0.507 | 1.4 | 1.23 | 1.4 | 1.41 | 1.4 | 1.26
1.6 | 0.224 | 1.6 | 0.357 | 1.6 | 0.574 | 1.6 | 1.39 | 1.6 | 1.61 | 1.6 | 1.46
1.8 | 0.25 | 1.8 | 0.397 | 1.8 | 0.642 | 1.8 | 1.55 | 1.8 | 1.81 | 1.8 | 1.66
2 | 0.277 | 2 | 0.436 | 2 | 0.713 | 2 | 1.71 | 2 | 2.01 | 2 | 1.88
2.2 | 0.303 | 2.2 | 0.475 | 2.2 | 0.786 | 2.2 | 1.88 | 2.2 | 2.21 | 2.2 | 2.09
2.4 | 0.328 | 2.4 | 0.515 | 2.4 | 0.86 | 2.4 | 2.04 | 2.4 | 2.41 | 2.4 | 2.31
2.6 | 0.352 | 2.6 | 0.555 | 2.6 | 0.936 | 2.6 | 2.21 | 2.6 | 2.61 | 2.6 | 2.52
2.8 | 0.375 | 2.8 | 0.595 | 2.8 | 1.01 | 2.8 | 2.38 | 2.8 | 2.8 | 2.8 | 2.73
3 | 0.397 | 3 | 0.636 | 3 | 1.09 | 3 | 2.55 | 3 | 2.99 | 3 | 2.93
3.2 | 0.418 | 3.2 | 0.677 | 3.2 | 1.17 | 3.2 | 2.72 | 3.2 | 3.17 | 3.2 | 3.13
3.4 | 0.439 | 3.4 | 0.718 | 3.4 | 1.24 | 3.4 | 2.88 | 3.4 | 3.34 | 3.4 | 3.32
3.6 | 0.46 | 3.6 | 0.76 | 3.6 | 1.31 | 3.6 | 3.03 | 3.6 | 3.51 | 3.6 | 3.49
3.8 | 0.482 | 3.8 | 0.8 | 3.8 | 1.38 | 3.8 | 3.18 | 3.8 | 3.66 | 3.8 | 3.65
4 | 0.506 | 4 | 0.839 | 4 | 1.44 | 4 | 3.31 | 4 | 3.8 | 4 | 3.8
Veriflow High 5,5 DN25L |  | Veriflow DN32 |  | Veriflow DN40 |  | Veriflow DN50
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
0.6 | 1.28 | 0.6 | 1.44 | 0.6 | 4.74 | 0.6 | 4.43
0.8 | 1.6847 | 0.8 | 1.8255 | 0.8 | 5.8162 | 0.8 | 5.3494
1 | 2.09 | 1 | 2.2 | 1 | 6.85 | 1 | 6.3
1.2 | 2.4913 | 1.2 | 2.5693 | 1.2 | 7.8621 | 1.2 | 7.2844
1.4 | 2.8855 | 1.4 | 2.9383 | 1.4 | 8.87 | 1.4 | 8.305
1.6 | 3.2704 | 1.6 | 3.311 | 1.6 | 9.8885 | 1.6 | 9.3636
1.8 | 3.6451 | 1.8 | 3.6908 | 1.8 | 10.929 | 1.8 | 10.4616
2 | 4.01 | 2 | 4.08 | 2 | 12 | 2 | 11.6
2.2 | 4.3665 | 2.2 | 4.4801 | 2.2 | 13.1071 | 2.2 | 12.7792
2.4 | 4.7173 | 2.4 | 4.8917 | 2.4 | 14.2528 | 2.4 | 13.9994
2.6 | 5.0663 | 2.6 | 5.3148 | 2.6 | 15.4364 | 2.6 | 15.2602
2.8 | 5.4184 | 2.8 | 5.7482 | 2.8 | 16.6543 | 2.8 | 16.5608
3 | 5.78 | 3 | 6.19 | 3 | 17.9 | 3 | 17.9
3.2 | 6.1584 | 3.2 | 6.6375 | 3.2 | 19.1638 | 3.2 | 18.74
3.4 | 6.5622 | 3.4 | 7.0872 | 3.4 | 20.4329 | 3.4 | 19.58
3.6 | 7.0012 | 3.6 | 7.5345 | 3.6 | 21.6916 | 3.6 | 20.42
3.8 | 7.4865 | 3.8 | 7.9742 | 3.8 | 22.9213 | 3.8 | 21.26
4 | 8.03 | 4 | 8.4 | 4 | 24.1 | 4 | 22.1

## OPTIMA Compact Veriflow fl FCP
QUICK - CONTROL OPTIMA Compact Veriflow Flanged
Flow Commissioning program
Input
∆P measured = | 15 | kPa (Use PT plugs P1 & P2)
Pre-set = | 4
Dimension | Range | Verification
| Flow (m3/h) | Flow (m3/h)
DN50 Ultra High Flow | 1.40-11.5 | 8.2882
DN50 Standard Low Flow | 2.50-15.0 | 15.337
DN50 Standard High Flow | 3.90-24.0 | 15.1434
DN65 Ultra Low Flow | 3.00-16.0 | 17.196
DN65 Ultra High Flow | 4.20-24.0 | 15.2208
DN65 Standard Low Flow | 4.40-25.0 | 20.9141
DN65 Standard High Flow | 6.00-35.0 | 21.0303
DN80 Ultra Low Flow | 4.40-25.0 | 20.9528
DN80 Ultra High Flow | 6.00-35.0 | 20.2557
DN80 Standard Low Flow | 5.30-34.0 | 29.1248
DN80 Standard High Flow | 7.00-43.0 | 29.2023
DN100 Ultra Low Flow | 5.30-34.0 | 30.7515
DN100 Ultra High Flow | 7.00-43.0 | 29.4347
DN100 Standard Low Flow | 12.1-68.0 | 65.0661
DN100 Standard High Flow | 14.8-90.0 | 68.9391
DN125 Ultra Low Flow | 12.1-68.0 | 58.482
DN125 Ultra High Flow | 14.8-90.0 | 69.3264
DN125 Standard Low Flow | 18.5-110 | 85.5929
DN125 Standard High Flow | 23.0-135 | 86.3675
DN150 Standard Low Flow | 25.6-148 | 104.9578
DN150 Standard High Flow | 32.0-195 | 107.2816
DN200 Standard Low Flow | 95.0-210 | 156.4685
DN200 Standard High Flow | 130-280 | 158.405
DN250 Standard Low Flow | 190-475 | 270.7215
DN250 Standard High Flow | 245-600 | 289.6992
DN300 Standard Low Flow | 190-475 | 269.9469
DN300 Standard High Flow | 245-600 | 288.9246
OPTIMA Veriflow Ultra DN50 HF |  | OPTIMA Veriflow Standard DN50 LF |  | OPTIMA Veriflow Standard DN50 HF |  | OPTIMA Veriflow Ultra DN65 LF |  | OPTIMA Veriflow Ultra DN65 HF |  | OPTIMA Veriflow Standard DN65 LF |  | OPTIMA Veriflow Standard DN65 HF
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
0.6 | 4.66 | 0.6 | 9.19 | 0.6 | 9.68 | 0.6 | 9.89 | 0.6 | 9.44 | 0.6 | 11.6 | 0.6 | 10.9
0.8 | 5.87 | 0.8 | 11.6904 | 0.8 | 11.9459 | 0.8 | 12.3 | 0.8 | 11.9 | 0.8 | 14.778 | 0.8 | 13.5956
1 | 7.11 | 1 | 13.9 | 1 | 14.1 | 1 | 14.4 | 1 | 14 | 1 | 17.5 | 1 | 16
1.2 | 8.34 | 1.2 | 15.8913 | 1.2 | 16.167 | 1.2 | 16.3 | 1.2 | 15.9 | 1.2 | 19.9096 | 1.2 | 18.2372
1.4 | 9.54 | 1.4 | 17.7274 | 1.4 | 18.167 | 1.4 | 18 | 1.4 | 17.7 | 1.4 | 22.1304 | 1.4 | 20.4114
1.6 | 10.7 | 1.6 | 19.4625 | 1.6 | 20.1158 | 1.6 | 19.7 | 1.6 | 19.5 | 1.6 | 24.2664 | 1.6 | 22.6068
1.8 | 11.7 | 1.8 | 21.1414 | 1.8 | 22.0245 | 1.8 | 21.5 | 1.8 | 21.2 | 1.8 | 26.4015 | 1.8 | 24.8881
2 | 12.7 | 2 | 22.8 | 2 | 23.9 | 2 | 23.4 | 2 | 22.9 | 2 | 28.6 | 2 | 27.3
2.2 | 13.6 | 2.2 | 24.4649 | 2.2 | 25.7444 | 2.2 | 25.4 | 2.2 | 24.7 | 2.2 | 30.9062 | 2.2 | 29.8675
2.4 | 14.4 | 2.4 | 26.1536 | 2.4 | 27.5556 | 2.4 | 27.5 | 2.4 | 26.5 | 2.4 | 33.3446 | 2.4 | 32.5957
2.6 | 15.1 | 2.6 | 27.8744 | 2.6 | 29.3268 | 2.6 | 29.8 | 2.6 | 28.3 | 2.6 | 35.9198 | 2.6 | 35.4701
2.8 | 15.8 | 2.8 | 29.6265 | 2.8 | 31.0468 | 2.8 | 32.2 | 2.8 | 30.1 | 2.8 | 38.6166 | 2.8 | 38.4563
3 | 16.5 | 3 | 31.4 | 3 | 32.7 | 3 | 34.6 | 3 | 32 | 3 | 41.4 | 3 | 41.5
3.2 | 17.2 | 3.2 | 33.1758 | 3.2 | 34.2661 | 3.2 | 37 | 3.2 | 33.8 | 3.2 | 44.2151 | 3.2 | 44.5273
3.4 | 18 | 3.4 | 34.9257 | 3.4 | 35.7206 | 3.4 | 39.3 | 3.4 | 35.5 | 3.4 | 46.9872 | 3.4 | 47.4444
3.6 | 18.9 | 3.6 | 36.6122 | 3.6 | 37.0342 | 3.6 | 41.4 | 3.6 | 37.1 | 3.6 | 49.6216 | 3.6 | 50.1378
3.8 | 20 | 3.8 | 38.1889 | 3.8 | 38.1734 | 3.8 | 43.1 | 3.8 | 38.3 | 3.8 | 52.004 | 3.8 | 52.474
4 | 21.4 | 4 | 39.6 | 4 | 39.1 | 4 | 44.4 | 4 | 39.3 | 4 | 54 | 4 | 54.3
OPTIMA Veriflow Ultra DN80 LF |  | OPTIMA Veriflow Ultra DN80 HF |  | OPTIMA Veriflow Standard DN80 LF |  | OPTIMA Veriflow Standard DN80 HF |  | OPTIMA Veriflow Ultra DN100 LF |  | OPTIMA Veriflow Ultra DN100 HF |  | OPTIMA Veriflow Standard DN100 LF |  | OPTIMA Veriflow Standard DN100 HF
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
0.6 | 10.4 | 0.6 | 10.8 | 0.6 | 14.9 | 0.6 | 15 | 0.6 | 15.6 | 0.6 | 16.8 | 0.6 | 35.2 | 0.6 | 35
0.8 | 12.8 | 0.8 | 13.2 | 0.8 | 18.7936 | 0.8 | 19.9303 | 0.8 | 19.2 | 0.8 | 19.9 | 0.8 | 43.3802 | 0.8 | 43.0131
1 | 15.2 | 1 | 15.5 | 1 | 22.4 | 1 | 24 | 1 | 22.6 | 1 | 23.1 | 1 | 50.2 | 1 | 49.6
1.2 | 17.5 | 1.2 | 17.9 | 1.2 | 25.8228 | 1.2 | 27.4924 | 1.2 | 26 | 1.2 | 26.3 | 1.2 | 56.0825 | 1.2 | 55.3489
1.4 | 19.9 | 1.4 | 20.2 | 1.4 | 29.1498 | 1.4 | 30.6493 | 1.4 | 29.4 | 1.4 | 29.7 | 1.4 | 61.4051 | 1.4 | 60.7644
1.6 | 22.2 | 1.6 | 22.7 | 1.6 | 32.4532 | 1.6 | 33.6708 | 1.6 | 33 | 1.6 | 33.1 | 1.6 | 66.4993 | 1.6 | 66.2673
1.8 | 24.5 | 1.8 | 25.1 | 1.8 | 35.7896 | 1.8 | 36.7154 | 1.8 | 36.6 | 1.8 | 36.7 | 1.8 | 71.6509 | 1.8 | 72.1947
2 | 26.9 | 2 | 27.6 | 2 | 39.2 | 2 | 39.9 | 2 | 40.5 | 2 | 40.5 | 2 | 77.1 | 2 | 78.8
2.2 | 29.3 | 2.2 | 30.1 | 2.2 | 42.7097 | 2.2 | 43.2998 | 2.2 | 44.5 | 2.2 | 44.4 | 2.2 | 83.0406 | 2.2 | 86.2528
2.4 | 31.7 | 2.4 | 32.7 | 2.4 | 46.3283 | 2.4 | 46.9485 | 2.4 | 48.7 | 2.4 | 48.4 | 2.4 | 89.6213 | 2.4 | 94.6389
2.6 | 34.2 | 2.6 | 35.2 | 2.6 | 50.0499 | 2.6 | 50.8381 | 2.6 | 53 | 2.6 | 52.4 | 2.6 | 96.9445 | 2.6 | 103.9605
2.8 | 36.8 | 2.8 | 37.8 | 2.8 | 53.8529 | 2.8 | 54.919 | 2.8 | 57.4 | 2.8 | 56.4 | 2.8 | 105.067 | 2.8 | 114.136
3 | 39.4 | 3 | 40.4 | 3 | 57.7 | 3 | 59.1 | 3 | 61.8 | 3 | 60.4 | 3 | 114 | 3 | 125
3.2 | 42.1 | 3.2 | 42.9 | 3.2 | 61.5384 | 3.2 | 63.2482 | 3.2 | 66.1 | 3.2 | 64.2 | 3.2 | 123.7085 | 3.2 | 136.3035
3.4 | 44.9 | 3.4 | 45.4 | 3.4 | 65.2996 | 3.4 | 67.1892 | 3.4 | 70.1 | 3.4 | 67.8 | 3.4 | 134.1121 | 3.4 | 147.7137
3.6 | 47.9 | 3.6 | 47.8 | 3.6 | 68.8994 | 3.6 | 70.7069 | 3.6 | 73.8 | 3.6 | 71.1 | 3.6 | 145.0843 | 3.6 | 158.814
3.8 | 50.9 | 3.8 | 50.1 | 3.8 | 72.238 | 3.8 | 73.5436 | 3.8 | 76.9 | 3.8 | 73.8 | 3.8 | 156.4529 | 3.8 | 169.1041
4 | 54.1 | 4 | 52.3 | 4 | 75.2 | 4 | 75.4 | 4 | 79.4 | 4 | 76 | 4 | 168 | 4 | 178
OPTIMA Veriflow Ultra DN125 LF |  | OPTIMA Veriflow Ultra DN125 HF |  | OPTIMA Veriflow Standard DN125 LF |  | OPTIMA Veriflow Standard DN125 HF
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
0.6 | 32.4 | 0.6 | 30.4 | 0.6 | 43.6 | 0.6 | 45.4
0.8 | 39.4 | 0.8 | 38.3 | 0.8 | 54.262 | 0.8 | 56.7184
1 | 45.7 | 1 | 45.9 | 1 | 64.4 | 1 | 67.4
1.2 | 51.4 | 1.2 | 53.2 | 1.2 | 74.2051 | 1.2 | 77.6724
1.4 | 56.9 | 1.4 | 60.2 | 1.4 | 83.8422 | 1.4 | 87.7282
1.6 | 62.2 | 1.6 | 67 | 1.6 | 93.4499 | 1.6 | 97.7252
1.8 | 67.7 | 1.8 | 73.7 | 1.8 | 103.1405 | 1.8 | 107.7864
2 | 73.4 | 2 | 80.4 | 2 | 113 | 2 | 118
2.2 | 79.4 | 2.2 | 87.2 | 2.2 | 123.0881 | 2.2 | 128.4193
2.4 | 85.9 | 2.4 | 94.2 | 2.4 | 133.4382 | 2.4 | 139.0627
2.6 | 92.8 | 2.6 | 102 | 2.6 | 144.0574 | 2.6 | 149.9139
2.8 | 100 | 2.8 | 109 | 2.8 | 154.9265 | 2.8 | 160.9217
3 | 108 | 3 | 118 | 3 | 166 | 3 | 172
3.2 | 116 | 3.2 | 127 | 3.2 | 177.2061 | 3.2 | 183.028
3.4 | 125 | 3.4 | 138 | 3.4 | 188.4467 | 3.4 | 193.85
3.6 | 134 | 3.6 | 150 | 3.6 | 199.5974 | 3.6 | 204.2754
3.8 | 142 | 3.8 | 164 | 3.8 | 210.5075 | 3.8 | 214.0788
4 | 151 | 4 | 179 | 4 | 221 | 4 | 223
OPTIMA Veriflow Standard DN150 LF |  | OPTIMA Veriflow Standard DN150 HF
Preset | KV signal | Preset | KV signal
0.6 | 60.8 | 0.6 | 59.8
0.8 | 77.0376 | 0.8 | 76.1074
1 | 92.3 | 1 | 91.6
1.2 | 106.7885 | 1.2 | 106.4142
1.4 | 120.6751 | 1.4 | 120.6689
1.6 | 134.1021 | 1.6 | 134.4654
1.8 | 147.1826 | 1.8 | 147.8871
2 | 160 | 2 | 161
2.2 | 172.6083 | 2.2 | 173.8522
2.4 | 185.0322 | 2.4 | 186.4743
2.6 | 197.2666 | 2.6 | 198.8791
2.8 | 209.2771 | 2.8 | 211.0618
3 | 221 | 3 | 223
3.2 | 232.3418 | 3.2 | 234.6535
3.4 | 243.1797 | 3.4 | 245.9646
3.6 | 253.3615 | 3.6 | 256.8577
3.8 | 262.7053 | 3.8 | 267.2398
4 | 271 | 4 | 277
OPTIMA Veriflow Standard DN200 LF |  | OPTIMA Veriflow Standard DN200 HF |  | OPTIMA Veriflow Standard DN250 LF |  | OPTIMA Veriflow Standard DN250 HF |  | OPTIMA Veriflow Standard DN300 LF |  | OPTIMA Veriflow Standard DN300 HF
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
1 | 243 | 1 | 245 | 1 | 408 | 1 | 428 | 1 | 387 | 1 | 397
1.2 | 261.368 | 1.2 | 264.52 | 1.2 | 417.824 | 1.2 | 442 | 1.2 | 419.464 | 1.2 | 429.432
1.4 | 275.664 | 1.4 | 279.52 | 1.4 | 431.512 | 1.4 | 456 | 1.4 | 446.672 | 1.4 | 457.296
1.6 | 286.576 | 1.6 | 290.76 | 1.6 | 448.488 | 1.6 | 470 | 1.6 | 469.448 | 1.6 | 481.344
1.8 | 294.792 | 1.8 | 299 | 1.8 | 468.176 | 1.8 | 484 | 1.8 | 488.616 | 1.8 | 502.328
2 | 301 | 2 | 305 | 2 | 490 | 2 | 498 | 2 | 505 | 2 | 521
2.2 | 305.888 | 2.2 | 309.52 | 2.2 | 513.384 | 2.2 | 533.44 | 2.2 | 519.424 | 2.2 | 538.112
2.4 | 310.144 | 2.4 | 313.32 | 2.4 | 537.752 | 2.4 | 566.56 | 2.4 | 532.712 | 2.4 | 554.416
2.6 | 314.456 | 2.6 | 317.16 | 2.6 | 562.528 | 2.6 | 597.36 | 2.6 | 545.688 | 2.6 | 570.664
2.8 | 319.512 | 2.8 | 321.8 | 2.8 | 587.136 | 2.8 | 625.84 | 2.8 | 559.176 | 2.8 | 587.608
3 | 326 | 3 | 328 | 3 | 611 | 3 | 652 | 3 | 574 | 3 | 606
3.2 | 334.608 | 3.2 | 336.52 | 3.2 | 633.544 | 3.2 | 675.84 | 3.2 | 590.984 | 3.2 | 626.592
3.4 | 346.024 | 3.4 | 348.12 | 3.4 | 654.192 | 3.4 | 697.36 | 3.4 | 610.952 | 3.4 | 650.136
3.6 | 360.936 | 3.6 | 363.56 | 3.6 | 672.368 | 3.6 | 716.56 | 3.6 | 634.728 | 3.6 | 677.384
3.8 | 380.032 | 3.8 | 383.6 | 3.8 | 687.496 | 3.8 | 733.44 | 3.8 | 663.136 | 3.8 | 709.088
4 | 404 | 4 | 409 | 4 | 699 | 4 | 748 | 4 | 697 | 4 | 746
P1
P2
P3

## Frese VODRV FCP
QUICK - CONTROL Frese STBV, VODRV
Flow Commissioning program
Input
| ∆P measured = | 100 | (kPa) KV signal (For flow measurement)
| Pre-set = | 4
DN | KV signal (Fully open valve) |  | Verification Flow (l/h)
15 | 6.8 |  | 6800
20 | 9.9 |  | 9880
25 | 31.8 |  | 31790
32 | 23 |  | 23010
40 | 40 |  | 39950
50 | 49.7 |  | 42700
| DN 15 |  | DN20 |  | DN25 |  | DN32 |  | DN40 |  | DN50
Einstellung | KV signal | KV total | KV signal | KV total | KV signal | KV total | KV signal | KV total | Einstellung | KV signal | KV signal | KV total
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.1 | 0.2 | 0.19 | 0.328 | 0.316 | 0.548 | 0.5 | 0.726 | 0.72 | 0.576 | 0.568 | 1.088 | 1.112
0.2 | 0.4 | 0.38 | 0.656 | 0.632 | 1.096 | 1 | 1.452 | 1.44 | 1.152 | 1.136 | 2.176 | 2.224
0.3 | 0.6 | 0.57 | 0.984 | 0.948 | 1.644 | 1.5 | 2.178 | 2.16 | 1.728 | 1.704 | 3.264 | 3.336
0.4 | 0.8 | 0.76 | 1.312 | 1.264 | 2.192 | 2 | 2.904 | 2.88 | 2.304 | 2.272 | 4.352 | 4.448
0.5 | 1 | 0.95 | 1.64 | 1.58 | 2.74 | 2.5 | 3.63 | 3.6 | 2.88 | 2.84 | 5.44 | 5.56
0.6 | 1.124 | 1.058 | 1.884 | 1.786 | 3.4026 | 2.914 | 4.358 | 4.312 | 3.972 | 3.936 | 6.75 | 6.916
0.7 | 1.248 | 1.166 | 2.128 | 1.992 | 4.0652 | 3.328 | 5.086 | 5.024 | 5.064 | 5.032 | 8.06 | 8.272
0.8 | 1.372 | 1.274 | 2.372 | 2.198 | 4.7278 | 3.742 | 5.814 | 5.736 | 6.156 | 6.128 | 9.37 | 9.628
0.9 | 1.496 | 1.382 | 2.616 | 2.404 | 5.3904 | 4.156 | 6.542 | 6.448 | 7.248 | 7.224 | 10.68 | 10.984
1 | 1.62 | 1.49 | 2.86 | 2.61 | 6.053 | 4.57 | 7.27 | 7.16 | 8.34 | 8.32 | 11.99 | 12.34
1.1 | 1.724 | 1.572 | 3.05 | 2.784 | 7.0844 | 4.946 | 8.018 | 7.822 | 9.496 | 9.276 | 13.122 | 13.39
1.2 | 1.828 | 1.654 | 3.24 | 2.958 | 8.1158 | 5.322 | 8.766 | 8.484 | 10.652 | 10.232 | 14.254 | 14.44
1.3 | 1.932 | 1.736 | 3.43 | 3.132 | 9.1472 | 5.698 | 9.514 | 9.146 | 11.808 | 11.188 | 15.386 | 15.49
1.4 | 2.036 | 1.818 | 3.62 | 3.306 | 10.1786 | 6.074 | 10.262 | 9.808 | 12.964 | 12.144 | 16.518 | 16.54
1.5 | 2.14 | 1.9 | 3.81 | 3.48 | 11.21 | 6.45 | 11.01 | 10.47 | 14.12 | 13.1 | 17.65 | 17.59
1.6 | 2.242 | 1.974 | 4.002 | 3.622 | 12.142 | 6.682 | 11.54 | 10.968 | 15.03 | 13.736 | 18.668 | 18.498
1.7 | 2.344 | 2.048 | 4.194 | 3.764 | 13.074 | 6.914 | 12.07 | 11.466 | 15.94 | 14.372 | 19.686 | 19.406
1.8 | 2.446 | 2.122 | 4.386 | 3.906 | 14.006 | 7.146 | 12.6 | 11.964 | 16.85 | 15.008 | 20.704 | 20.314
1.9 | 2.548 | 2.196 | 4.578 | 4.048 | 14.938 | 7.378 | 13.13 | 12.462 | 17.76 | 15.644 | 21.722 | 21.222
2 | 2.65 | 2.27 | 4.77 | 4.19 | 15.87 | 7.61 | 13.66 | 12.96 | 18.67 | 16.28 | 22.74 | 22.13
2.1 | 2.698 | 2.316 | 4.92 | 4.324 | 16.838 | 7.828 | 14.132 | 13.416 | 19.542 | 16.87 | 23.766 | 22.834
2.2 | 2.746 | 2.362 | 5.07 | 4.458 | 17.806 | 8.046 | 14.604 | 13.872 | 20.414 | 17.46 | 24.792 | 23.538
2.3 | 2.794 | 2.408 | 5.22 | 4.592 | 18.774 | 8.264 | 15.076 | 14.328 | 21.286 | 18.05 | 25.818 | 24.242
2.4 | 2.842 | 2.454 | 5.37 | 4.726 | 19.742 | 8.482 | 15.548 | 14.784 | 22.158 | 18.64 | 26.844 | 24.946
2.5 | 2.89 | 2.5 | 5.52 | 4.86 | 20.71 | 8.7 | 16.02 | 15.24 | 23.03 | 19.23 | 27.87 | 25.65
2.6 | 3.116 | 2.578 | 5.716 | 4.986 | 21.566 | 8.84 | 16.458 | 15.646 | 23.812 | 19.722 | 28.76 | 26.412
2.7 | 3.342 | 2.656 | 5.912 | 5.112 | 22.422 | 8.98 | 16.896 | 16.052 | 24.594 | 20.214 | 29.65 | 27.174
2.8 | 3.568 | 2.734 | 6.108 | 5.238 | 23.278 | 9.12 | 17.334 | 16.458 | 25.376 | 20.706 | 30.54 | 27.936
2.9 | 3.794 | 2.812 | 6.304 | 5.364 | 24.134 | 9.26 | 17.772 | 16.864 | 26.158 | 21.198 | 31.43 | 28.698
3 | 4.02 | 2.89 | 6.5 | 5.49 | 24.99 | 9.4 | 18.21 | 17.27 | 26.94 | 21.69 | 32.32 | 29.46
3.1 | 4.288 | 2.952 | 6.772 | 5.61 | 26.194 | 9.544 | 18.718 | 17.682 | 28.148 | 22.166 | 33.332 | 30.194
3.2 | 4.556 | 3.014 | 7.044 | 5.73 | 27.398 | 9.688 | 19.226 | 18.094 | 29.356 | 22.642 | 34.344 | 30.928
3.3 | 4.824 | 3.076 | 7.316 | 5.85 | 28.602 | 9.832 | 19.734 | 18.506 | 30.564 | 23.118 | 35.356 | 31.662
3.4 | 5.092 | 3.138 | 7.588 | 5.97 | 29.806 | 9.976 | 20.242 | 18.918 | 31.772 | 23.594 | 36.368 | 32.396
3.5 | 5.36 | 3.2 | 7.86 | 6.09 | 31.01 | 10.12 | 20.75 | 19.33 | 32.98 | 24.07 | 37.38 | 33.13
3.6 | 5.648 | 3.258 | 8.264 | 6.172 | 31.166 | 10.196 | 21.202 | 19.664 | 34.374 | 24.456 | 38.444 | 33.768
3.7 | 5.936 | 3.316 | 8.668 | 6.254 | 31.322 | 10.272 | 21.654 | 19.998 | 35.768 | 24.842 | 39.508 | 34.406
3.8 | 6.224 | 3.374 | 9.072 | 6.336 | 31.478 | 10.348 | 22.106 | 20.332 | 37.162 | 25.228 | 40.572 | 35.044
3.9 | 6.512 | 3.432 | 9.476 | 6.418 | 31.634 | 10.424 | 22.558 | 20.666 | 38.556 | 25.614 | 41.636 | 35.682
4 | 6.8 | 3.49 | 9.88 | 6.5 | 31.79 | 10.5 | 23.01 | 21 | 39.95 | 26 | 42.7 | 36.32
4.1 | [10 empty] | 44.1 | 37.056
4.2 | [10 empty] | 45.5 | 37.792
4.3 | [10 empty] | 46.9 | 38.528
4.4 | [10 empty] | 48.3 | 39.264
4.5 | [10 empty] | 49.7 | 40

## Frese VODRV flanged FCP 2024
QUICK - CONTROL Frese STBV, VODRV Flanged
Flow Commissioning program
Input
| ∆P measured = | 10 | (kPa) Total valve
| Pre-set = | 10
DN | KV (Fully open valve) |  | Verification Flow (m3/h)
65 | 94.6 |  | NOT POSSIBLE
80 | 119 |  | NOT POSSIBLE
100 | 215 |  | NOT POSSIBLE
125 | 289 |  | NOT POSSIBLE
150 | 403 |  | NOT POSSIBLE
200 | 852 |  | 269.4261
250 | 1240 |  | 325.7146
300 | 1420 |  | 325.7146
350 | 2085 |  | 325.1744
400 | 2189 |  | 361.72
450 | 2526 |  | 456.1867
500 | 3381 |  | 554.3703
| DN65 | DN80 | DN100 | DN125 | DN150 | DN200 | DN250 | DN300 | DN350 | DN400 | DN450 | DN500
Preset | KV | KV | KV | KV | KV | KV | KV | KV | KV | KV | KV | KV
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.1 | 0.3 | 0.57 | 0.9 | 0.97 | 1.41 | 4.84 | 6.99 | 9.36 | 16.8991 | 23.2404 | 25.4536 | 32.1578
0.2 | 0.6 | 1.14 | 1.8 | 1.94 | 2.82 | 9.68 | 13.98 | 18.72 | 33.7981 | 46.4808 | 50.9073 | 64.3155
0.3 | 0.9 | 1.71 | 2.7 | 2.91 | 4.23 | 14.52 | 20.97 | 28.08 | 50.6972 | 69.7212 | 76.3609 | 96.4733
0.4 | 1.2 | 2.28 | 3.6 | 3.88 | 5.64 | 19.36 | 27.96 | 37.44 | 67.5963 | 92.9616 | 101.8145 | 128.6311
0.5 | 1.5 | 2.85 | 4.5 | 4.85 | 7.05 | 24.2 | 34.95 | 46.8 | 84.4954 | 116.202 | 127.2681 | 160.7888
0.6 | 1.8 | 3.42 | 5.4 | 5.82 | 8.46 | 29.04 | 41.94 | 49.06 | 101.3944 | 139.4424 | 152.7218 | 192.9466
0.7 | 2.1 | 3.99 | 6.3 | 6.79 | 9.87 | 33.88 | 48.93 | 51.32 | 118.2935 | 162.6828 | 178.1754 | 225.1044
0.8 | 2.4 | 4.56 | 7.2 | 7.76 | 11.28 | 38.72 | 55.92 | 53.58 | 135.1926 | 185.9232 | 203.629 | 257.2621
0.9 | 2.7 | 5.13 | 8.1 | 8.73 | 12.69 | 43.56 | 62.91 | 55.84 | 152.0916 | 209.1636 | 229.0826 | 289.4199
1 | 3 | 5.7 | 9 | 9.7 | 14.1 | 48.4 | 69.9 | 58.1 | 168.9907 | 232.404 | 254.5363 | 321.5777
1.1 | 3.62 | 6.14 | 10.28 | 10.92 | 16.99 | 54.96 | 78.41 | 65.99 | 181.8949 | 247.5387 | 269.2989 | 345.9495
1.2 | 4.24 | 6.58 | 11.56 | 12.14 | 19.88 | 61.52 | 86.92 | 73.88 | 194.7992 | 262.6734 | 284.0616 | 370.3214
1.3 | 4.86 | 7.02 | 12.84 | 13.36 | 22.77 | 68.08 | 95.43 | 81.77 | 207.7034 | 277.8082 | 298.8242 | 394.6933
1.4 | 5.48 | 7.46 | 14.12 | 14.58 | 25.66 | 74.64 | 103.94 | 89.66 | 220.6076 | 292.9429 | 313.5869 | 419.0652
1.5 | 6.1 | 7.9 | 15.4 | 15.8 | 28.55 | 81.2 | 112.45 | 97.55 | 233.5119 | 308.0776 | 328.3495 | 443.437
1.6 | 6.72 | 8.34 | 16.68 | 17.02 | 31.44 | 87.76 | 120.96 | 105.44 | 246.4161 | 323.2123 | 343.1122 | 467.8089
1.7 | 7.34 | 8.78 | 17.96 | 18.24 | 34.33 | 94.32 | 129.47 | 113.33 | 259.3203 | 338.347 | 357.8749 | 492.1808
1.8 | 7.96 | 9.22 | 19.24 | 19.46 | 37.22 | 100.88 | 137.98 | 121.22 | 272.2246 | 353.4817 | 372.6375 | 516.5527
1.9 | 8.58 | 9.66 | 20.52 | 20.68 | 40.11 | 107.44 | 146.49 | 129.11 | 285.1288 | 368.6165 | 387.4002 | 540.9245
2 | 9.2 | 10.1 | 21.8 | 21.9 | 43 | 114 | 155 | 137 | 298.033 | 383.7512 | 402.1628 | 565.2964
2.1 | 10.17 | 10.77 | 24.15 | 24.99 | 48 | 119 | 163.9 | 144.9 | 311.5089 | 398.0993 | 418.4651 | 587.152
2.2 | 11.14 | 11.44 | 26.5 | 28.08 | 53 | 124 | 172.8 | 152.8 | 324.9848 | 412.4474 | 434.7673 | 609.0076
2.3 | 12.11 | 12.11 | 28.85 | 31.17 | 58 | 129 | 181.7 | 160.7 | 338.4607 | 426.7956 | 451.0696 | 630.8633
2.4 | 13.08 | 12.78 | 31.2 | 34.26 | 63 | 134 | 190.6 | 168.6 | 351.9366 | 441.1437 | 467.3719 | 652.7189
2.5 | 14.05 | 13.45 | 33.55 | 37.35 | 68 | 139 | 199.5 | 176.5 | 365.4125 | 455.4918 | 483.6741 | 674.5745
2.6 | 15.02 | 14.12 | 35.9 | 40.44 | 73 | 144 | 208.4 | 184.4 | 378.8884 | 469.8399 | 499.9764 | 696.4301
2.7 | 15.99 | 14.79 | 38.25 | 43.53 | 78 | 149 | 217.3 | 192.3 | 392.3643 | 484.1881 | 516.2786 | 718.2858
2.8 | 16.96 | 15.46 | 40.6 | 46.62 | 83 | 154 | 226.2 | 200.2 | 405.8402 | 498.5362 | 532.5809 | 740.1414
2.9 | 17.93 | 16.13 | 42.95 | 49.71 | 88 | 159 | 235.1 | 208.1 | 419.3161 | 512.8843 | 548.8832 | 761.997
3 | 18.9 | 16.8 | 45.3 | 52.8 | 93 | 164 | 244 | 216 | 432.792 | 527.2324 | 565.1854 | 783.8526
3.1 | 21.06 | 18.63 | 48.09 | 57.44 | 98.3 | 171.4 | 249.5 | 221.8 | 444.7623 | 541.2176 | 581.867 | 804.5787
3.2 | 23.22 | 20.46 | 50.88 | 62.08 | 103.6 | 178.8 | 255 | 227.6 | 456.7326 | 555.2027 | 598.5486 | 825.3048
3.3 | 25.38 | 22.29 | 53.67 | 66.72 | 108.9 | 186.2 | 260.5 | 233.4 | 468.7028 | 569.1879 | 615.2301 | 846.0308
3.4 | 27.54 | 24.12 | 56.46 | 71.36 | 114.2 | 193.6 | 266 | 239.2 | 480.6731 | 583.173 | 631.9117 | 866.7569
3.5 | 29.7 | 25.95 | 59.25 | 76 | 119.5 | 201 | 271.5 | 245 | 492.6434 | 597.1582 | 648.5933 | 887.483
3.6 | 31.86 | 27.78 | 62.04 | 80.64 | 124.8 | 208.4 | 277 | 250.8 | 504.6136 | 611.1433 | 665.2748 | 908.209
3.7 | 34.02 | 29.61 | 64.83 | 85.28 | 130.1 | 215.8 | 282.5 | 256.6 | 516.5839 | 625.1285 | 681.9564 | 928.9351
3.8 | 36.18 | 31.44 | 67.62 | 89.92 | 135.4 | 223.2 | 288 | 262.4 | 528.5542 | 639.1136 | 698.638 | 949.6612
3.9 | 38.34 | 33.27 | 70.41 | 94.56 | 140.7 | 230.6 | 293.5 | 268.2 | 540.5244 | 653.0987 | 715.3195 | 970.3872
4 | 40.5 | 35.1 | 73.2 | 99.2 | 146 | 238 | 299 | 274 | 552.4947 | 667.0839 | 732.0011 | 991.1133
4.1 | 42.61 | 37.94 | 77.56 | 105.47 | 151.7 | 253.4 | 310.5 | 279.5 | 565.0749 | 680.1528 | 746.04 | 1010.831
4.2 | 44.72 | 40.78 | 81.92 | 111.74 | 157.4 | 268.8 | 322 | 285 | 577.655 | 693.2217 | 760.0789 | 1030.5486
4.3 | 46.83 | 43.62 | 86.28 | 118.01 | 163.1 | 284.2 | 333.5 | 290.5 | 590.2351 | 706.2906 | 774.1178 | 1050.2663
4.4 | 48.94 | 46.46 | 90.64 | 124.28 | 168.8 | 299.6 | 345 | 296 | 602.8153 | 719.3594 | 788.1568 | 1069.9839
4.5 | 51.05 | 49.3 | 95 | 130.55 | 174.5 | 315 | 356.5 | 301.5 | 615.3954 | 732.4283 | 802.1957 | 1089.7016
4.6 | 53.16 | 52.14 | 99.36 | 136.82 | 180.2 | 330.4 | 368 | 307 | 627.9756 | 745.4972 | 816.2346 | 1109.4193
4.7 | 55.27 | 54.98 | 103.72 | 143.09 | 185.9 | 345.8 | 379.5 | 312.5 | 640.5557 | 758.5661 | 830.2735 | 1129.1369
4.8 | 57.38 | 57.82 | 108.08 | 149.36 | 191.6 | 361.2 | 391 | 318 | 653.1359 | 771.635 | 844.3124 | 1148.8546
4.9 | 59.49 | 60.66 | 112.44 | 155.63 | 197.3 | 376.6 | 402.5 | 323.5 | 665.716 | 784.7039 | 858.3513 | 1168.5723
5 | 61.6 | 63.5 | 116.8 | 161.9 | 203 | 392 | 414 | 329 | 678.2962 | 797.7728 | 872.3902 | 1188.2899
5.1 | 62.96 | 65.71 | 120.32 | 165.2 | 206.3 | 403.5 | 426.7 | 344.4 | 688.2255 | 808.4162 | 887.4938 | 1206.1978
5.2 | 64.32 | 67.92 | 123.84 | 168.5 | 209.6 | 415 | 439.4 | 359.8 | 698.1548 | 819.0596 | 902.5975 | 1224.1056
5.3 | 65.68 | 70.13 | 127.36 | 171.8 | 212.9 | 426.5 | 452.1 | 375.2 | 708.0841 | 829.703 | 917.7011 | 1242.0135
5.4 | 67.04 | 72.34 | 130.88 | 175.1 | 216.2 | 438 | 464.8 | 390.6 | 718.0134 | 840.3464 | 932.8047 | 1259.9213
5.5 | 68.4 | 74.55 | 134.4 | 178.4 | 219.5 | 449.5 | 477.5 | 406 | 727.9427 | 850.9898 | 947.9083 | 1277.8292
5.6 | 69.76 | 76.76 | 137.92 | 181.7 | 222.8 | 461 | 490.2 | 421.4 | 737.872 | 861.6332 | 963.012 | 1295.737
5.7 | 71.12 | 78.97 | 141.44 | 185 | 226.1 | 472.5 | 502.9 | 436.8 | 747.8013 | 872.2766 | 978.1156 | 1313.6448
5.8 | 72.48 | 81.18 | 144.96 | 188.3 | 229.4 | 484 | 515.6 | 452.2 | 757.7306 | 882.92 | 993.2192 | 1331.5527
5.9 | 73.84 | 83.39 | 148.48 | 191.6 | 232.7 | 495.5 | 528.3 | 467.6 | 767.6599 | 893.5633 | 1008.3228 | 1349.4605
6 | 75.2 | 85.6 | 152 | 194.9 | 236 | 507 | 541 | 483 | 777.5892 | 904.2067 | 1023.4265 | 1367.3684
6.1 | 76.09 | 87.03 | 154.73 | 198.51 | 241.6 | 516.7 | 553.2 | 496.3 | 786.8066 | 913.4261 | 1035.2657 | 1380.8412
6.2 | 76.98 | 88.46 | 157.46 | 202.12 | 247.2 | 526.4 | 565.4 | 509.6 | 796.024 | 922.6455 | 1047.105 | 1394.314
6.3 | 77.87 | 89.89 | 160.19 | 205.73 | 252.8 | 536.1 | 577.6 | 522.9 | 805.2414 | 931.8648 | 1058.9443 | 1407.7869
6.4 | 78.76 | 91.32 | 162.92 | 209.34 | 258.4 | 545.8 | 589.8 | 536.2 | 814.4588 | 941.0842 | 1070.7836 | 1421.2597
6.5 | 79.65 | 92.75 | 165.65 | 212.95 | 264 | 555.5 | 602 | 549.5 | 823.6762 | 950.3036 | 1082.6229 | 1434.7325
6.6 | 80.54 | 94.18 | 168.38 | 216.56 | 269.6 | 565.2 | 614.2 | 562.8 | 832.8936 | 959.5229 | 1094.4622 | 1448.2053
6.7 | 81.43 | 95.61 | 171.11 | 220.17 | 275.2 | 574.9 | 626.4 | 576.1 | 842.111 | 968.7423 | 1106.3014 | 1461.6781
6.8 | 82.32 | 97.04 | 173.84 | 223.78 | 280.8 | 584.6 | 638.6 | 589.4 | 851.3284 | 977.9616 | 1118.1407 | 1475.151
6.9 | 83.21 | 98.47 | 176.57 | 227.39 | 286.4 | 594.3 | 650.8 | 602.7 | 860.5458 | 987.181 | 1129.98 | 1488.6238
7 | 84.1 | 99.9 | 179.3 | 231 | 292 | 604 | 663 | 616 | 869.7632 | 996.4004 | 1141.8193 | 1502.0966
7.1 | 84.76 | 100.85 | 181.66 | 233.86 | 297.8 | 612.6 | 675.3 | 629.6 | 878.1781 | 1004.7412 | 1155.5018 | 1512.7934
7.2 | 85.42 | 101.8 | 184.02 | 236.72 | 303.6 | 621.2 | 687.6 | 643.2 | 886.5931 | 1013.0821 | 1169.1844 | 1523.4903
7.3 | 86.08 | 102.75 | 186.38 | 239.58 | 309.4 | 629.8 | 699.9 | 656.8 | 895.008 | 1021.423 | 1182.8669 | 1534.1871
7.4 | 86.74 | 103.7 | 188.74 | 242.44 | 315.2 | 638.4 | 712.2 | 670.4 | 903.4229 | 1029.7639 | 1196.5495 | 1544.8839
7.5 | 87.4 | 104.65 | 191.1 | 245.3 | 321 | 647 | 724.5 | 684 | 911.8379 | 1038.1047 | 1210.2321 | 1555.5807
7.6 | 88.06 | 105.6 | 193.46 | 248.16 | 326.8 | 655.6 | 736.8 | 697.6 | 920.2528 | 1046.4456 | 1223.9146 | 1566.2776
7.7 | 88.72 | 106.55 | 195.82 | 251.02 | 332.6 | 664.2 | 749.1 | 711.2 | 928.6678 | 1054.7865 | 1237.5972 | 1576.9744
7.8 | 89.38 | 107.5 | 198.18 | 253.88 | 338.4 | 672.8 | 761.4 | 724.8 | 937.0827 | 1063.1274 | 1251.2797 | 1587.6712
7.9 | 90.04 | 108.45 | 200.54 | 256.74 | 344.2 | 681.4 | 773.7 | 738.4 | 945.4976 | 1071.4682 | 1264.9623 | 1598.368
8 | 90.7 | 109.4 | 202.9 | 259.6 | 350 | 690 | 786 | 752 | 953.9126 | 1079.8091 | 1278.6448 | 1609.0649
8.1 | 91.09 | 110.36 | 204.11 | 262.54 | 355.3 | 699.3 | 799.1 | 765.3 | 959.0791 | 1083.8874 | 1284.3629 | 1618.2765
8.2 | 91.48 | 111.32 | 205.32 | 265.48 | 360.6 | 708.6 | 812.2 | 778.6 | 964.2455 | 1087.9657 | 1290.081 | 1627.4881
8.3 | 91.87 | 112.28 | 206.53 | 268.42 | 365.9 | 717.9 | 825.3 | 791.9 | 969.412 | 1092.044 | 1295.7991 | 1636.6997
8.4 | 92.26 | 113.24 | 207.74 | 271.36 | 371.2 | 727.2 | 838.4 | 805.2 | 974.5785 | 1096.1223 | 1301.5172 | 1645.9113
8.5 | 92.65 | 114.2 | 208.95 | 274.3 | 376.5 | 736.5 | 851.5 | 818.5 | 979.7449 | 1100.2006 | 1307.2353 | 1655.1229
8.6 | 93.04 | 115.16 | 210.16 | 277.24 | 381.8 | 745.8 | 864.6 | 831.8 | 984.9114 | 1104.2789 | 1312.9533 | 1664.3345
8.7 | 93.43 | 116.12 | 211.37 | 280.18 | 387.1 | 755.1 | 877.7 | 845.1 | 990.0779 | 1108.3572 | 1318.6714 | 1673.5461
8.8 | 93.82 | 117.08 | 212.58 | 283.12 | 392.4 | 764.4 | 890.8 | 858.4 | 995.2444 | 1112.4355 | 1324.3895 | 1682.7577
8.9 | 94.21 | 118.04 | 213.79 | 286.06 | 397.7 | 773.7 | 903.9 | 871.7 | 1000.4108 | 1116.5138 | 1330.1076 | 1691.9693
9 | 94.6 | 119 | 215 | 289 | 403 | 783 | 917 | 885 | 1005.5773 | 1120.5921 | 1335.8257 | 1701.1809
9.1 | [5 empty] | 789.9 | 928.3 | 899.5 | 1007.8488 | 1122.9188 | 1346.502 | 1706.3701
9.2 | [5 empty] | 796.8 | 939.6 | 914 | 1010.1202 | 1125.2455 | 1357.1783 | 1711.5593
9.3 | [5 empty] | 803.7 | 950.9 | 928.5 | 1012.3917 | 1127.5722 | 1367.8546 | 1716.7485
9.4 | [5 empty] | 810.6 | 962.2 | 943 | 1014.6631 | 1129.8989 | 1378.531 | 1721.9377
9.5 | [5 empty] | 817 | 973.5 | 957.5 | 1016.9346 | 1132.2256 | 1389.2073 | 1727.1269
9.6 | [5 empty] | 824.4 | 984.8 | 972 | 1019.206 | 1134.5523 | 1399.8836 | 1732.3161
9.7 | [5 empty] | 831.3 | 996.1 | 986.5 | 1021.4775 | 1136.879 | 1410.5599 | 1737.5053
9.8 | [5 empty] | 838.2 | 1007.4 | 1001 | 1023.7489 | 1139.2057 | 1421.2363 | 1742.6945
9.9 | [5 empty] | 845.1 | 1018.7 | 1015.5 | 1026.0204 | 1141.5324 | 1431.9126 | 1747.8837
10 | [5 empty] | 852 | 1030 | 1030 | 1028.2918 | 1143.8591 | 1442.5889 | 1753.0729
10.1 | [6 empty] | 1041 | 1043 | 1037.7459 | 1146.9471 | 1454.0802 | 1756.6543
10.2 | [6 empty] | 1052 | 1056 | 1047.2 | 1150.0352 | 1465.5714 | 1760.2358
10.3 | [6 empty] | 1063 | 1069 | 1056.654 | 1153.1232 | 1477.0627 | 1763.8172
10.4 | [6 empty] | 1074 | 1082 | 1066.1081 | 1156.2113 | 1488.554 | 1767.3986
10.5 | [6 empty] | 1085 | 1095 | 1075.5622 | 1159.2993 | 1500.0452 | 1770.98
10.6 | [6 empty] | 1096 | 1108 | 1085.0162 | 1162.3873 | 1511.5365 | 1774.5615
10.7 | [6 empty] | 1107 | 1121 | 1094.4703 | 1165.4754 | 1523.0277 | 1778.1429
10.8 | [6 empty] | 1118 | 1134 | 1103.9243 | 1168.5634 | 1534.519 | 1781.7243
10.9 | [6 empty] | 1129 | 1147 | 1113.3784 | 1171.6514 | 1546.0103 | 1785.3057
11 | [6 empty] | 1140 | 1160 | 1122.8325 | 1174.7395 | 1557.5015 | 1788.8871
11.1 | [6 empty] | 1150 | 1173 | 1136.1469 | 1184.2658 | 1559.6441 | 1802.1741
11.2 | [6 empty] | 1160 | 1186 | 1149.4613 | 1193.7922 | 1561.7868 | 1815.461
11.3 | [6 empty] | 1170 | 1199 | 1162.7757 | 1203.3185 | 1563.9294 | 1828.748
11.4 | [6 empty] | 1180 | 1212 | 1176.0901 | 1212.8448 | 1566.072 | 1842.0349
11.5 | [6 empty] | 1190 | 1225 | 1189.4045 | 1222.3712 | 1568.2146 | 1855.3219
11.6 | [6 empty] | 1200 | 1238 | 1202.7189 | 1231.8975 | 1570.3572 | 1868.6088
11.7 | [6 empty] | 1210 | 1251 | 1216.0333 | 1241.4239 | 1572.4998 | 1881.8958
11.8 | [6 empty] | 1220 | 1264 | 1229.3477 | 1250.9502 | 1574.6424 | 1895.1827
11.9 | [6 empty] | 1230 | 1277 | 1242.6621 | 1260.4766 | 1576.785 | 1908.4697
12 | [6 empty] | 1240 | 1290 | 1255.9765 | 1270.0029 | 1578.9277 | 1921.7566
12.1 | [7 empty] | 1303 | 1267.2721 | 1283.2481 | 1580.2658 | 1941.1449
12.2 | [7 empty] | 1316 | 1278.5677 | 1296.4934 | 1581.604 | 1960.5332
12.3 | [7 empty] | 1329 | 1289.8632 | 1309.7386 | 1582.9422 | 1979.9216
12.4 | [7 empty] | 1342 | 1301.1588 | 1322.9838 | 1584.2804 | 1999.3099
12.5 | [7 empty] | 1355 | 1312.4543 | 1336.229 | 1585.6186 | 2018.6982
12.6 | [7 empty] | 1368 | 1323.7499 | 1349.4742 | 1586.9568 | 2038.0865
12.7 | [7 empty] | 1381 | 1335.0454 | 1362.7195 | 1588.295 | 2057.4749
12.8 | [7 empty] | 1394 | 1346.341 | 1375.9647 | 1589.6332 | 2076.8632
12.9 | [7 empty] | 1407 | 1357.6365 | 1389.2099 | 1590.9714 | 2096.2515
13 | [7 empty] | 1420 | 1368.9321 | 1402.4551 | 1592.3095 | 2115.6398
13.1 | [8 empty] | 1376.847 | 1415.4352 | 1606.5187 | 2134.6828
13.2 | [8 empty] | 1384.7619 | 1428.4153 | 1620.7279 | 2153.7257
13.3 | [8 empty] | 1392.6768 | 1441.3954 | 1634.9371 | 2172.7686
13.4 | [8 empty] | 1400.5917 | 1454.3755 | 1649.1463 | 2191.8116
13.5 | [8 empty] | 1408.5066 | 1467.3556 | 1663.3555 | 2210.8545
13.6 | [8 empty] | 1416.4215 | 1480.3357 | 1677.5647 | 2229.8975
13.7 | [8 empty] | 1424.3363 | 1493.3158 | 1691.7739 | 2248.9404
13.8 | [8 empty] | 1432.2512 | 1506.2959 | 1705.9831 | 2267.9833
13.9 | [8 empty] | 1440.1661 | 1519.276 | 1720.1923 | 2287.0263
14 | [8 empty] | 1448.081 | 1532.2561 | 1734.4015 | 2306.0692
14.1 | [8 empty] | 1460.338 | 1545.6621 | 1741.3878 | 2325.8085
14.2 | [8 empty] | 1472.595 | 1559.0682 | 1748.374 | 2345.5479
14.3 | [8 empty] | 1484.8521 | 1572.4742 | 1755.3602 | 2365.2872
14.4 | [8 empty] | 1497.1091 | 1585.8802 | 1762.3464 | 2385.0265
14.5 | [8 empty] | 1509.3661 | 1599.2863 | 1769.3327 | 2404.7659
14.6 | [8 empty] | 1521.6231 | 1612.6923 | 1776.3189 | 2424.5052
14.7 | [8 empty] | 1533.8801 | 1626.0983 | 1783.3051 | 2444.2445
14.8 | [8 empty] | 1546.1371 | 1639.5044 | 1790.2913 | 2463.9839
14.9 | [8 empty] | 1558.3941 | 1652.9104 | 1797.2776 | 2483.7232
15 | [8 empty] | 1570.6511 | 1666.3164 | 1804.2638 | 2503.4625
15.1 | [8 empty] | 1583.2076 | 1678.5452 | 1820.7239 | 2525.4659
15.2 | [8 empty] | 1595.764 | 1690.7739 | 1837.1841 | 2547.4694
15.3 | [8 empty] | 1608.3204 | 1703.0027 | 1853.6442 | 2569.4728
15.4 | [8 empty] | 1620.8769 | 1715.2314 | 1870.1044 | 2591.4762
15.5 | [8 empty] | 1633.4333 | 1727.4602 | 1886.5645 | 2613.4796
15.6 | [8 empty] | 1645.9897 | 1739.689 | 1903.0246 | 2635.483
15.7 | [8 empty] | 1658.5462 | 1751.9177 | 1919.4848 | 2657.4864
15.8 | [8 empty] | 1671.1026 | 1764.1465 | 1935.9449 | 2679.4899
15.9 | [8 empty] | 1683.659 | 1776.3752 | 1952.4051 | 2701.4933
16 | [8 empty] | 1696.2155 | 1788.604 | 1968.8652 | 2723.4967
16.1 | [8 empty] | 1709.8092 | 1803.3003 | 1985.9806 | 2743.528
16.2 | [8 empty] | 1723.403 | 1817.9967 | 2003.096 | 2763.5593
16.3 | [8 empty] | 1736.9967 | 1832.6931 | 2020.2114 | 2783.5907
16.4 | [8 empty] | 1750.5905 | 1847.3894 | 2037.3268 | 2803.622
16.5 | [8 empty] | 1764.1842 | 1862.0858 | 2054.4422 | 2823.6533
16.6 | [8 empty] | 1777.778 | 1876.7822 | 2071.5576 | 2843.6847
16.7 | [8 empty] | 1791.3717 | 1891.4785 | 2088.673 | 2863.716
16.8 | [8 empty] | 1804.9655 | 1906.1749 | 2105.7884 | 2883.7473
16.9 | [8 empty] | 1818.5593 | 1920.8712 | 2122.9038 | 2903.7786
17 | [8 empty] | 1832.153 | 1935.5676 | 2140.0192 | 2923.81
17.1 | [8 empty] | 1842.4906 | 1951.0868 | 2158.2217 | 2945.2512
17.2 | [8 empty] | 1852.8283 | 1966.6061 | 2176.4243 | 2966.6924
17.3 | [8 empty] | 1863.1659 | 1982.1253 | 2194.6268 | 2988.1336
17.4 | [8 empty] | 1873.5035 | 1997.6446 | 2212.8294 | 3009.5748
17.5 | [8 empty] | 1883.8411 | 2013.1638 | 2231.0319 | 3031.016
17.6 | [8 empty] | 1894.1787 | 2028.6831 | 2249.2345 | 3052.4572
17.7 | [8 empty] | 1904.5164 | 2044.2023 | 2267.4371 | 3073.8984
17.8 | [8 empty] | 1914.854 | 2059.7216 | 2285.6396 | 3095.3396
17.9 | [8 empty] | 1925.1916 | 2075.2408 | 2303.8422 | 3116.7809
18 | [8 empty] | 1935.5292 | 2090.76 | 2322.0447 | 3138.2221
18.1 | [8 empty] | 1950.4763 | 2100.584 | 2342.4402 | 3162.4999
18.2 | [8 empty] | 1965.4234 | 2110.408 | 2362.8358 | 3186.7777
18.3 | [8 empty] | 1980.3705 | 2120.232 | 2383.2313 | 3211.0554
18.4 | [8 empty] | 1995.3175 | 2130.056 | 2403.6268 | 3235.3332
18.5 | [8 empty] | 2010.2646 | 2139.88 | 2424.0224 | 3259.611
18.6 | [8 empty] | 2025.2117 | 2149.704 | 2444.4179 | 3283.8888
18.7 | [8 empty] | 2040.1588 | 2159.528 | 2464.8134 | 3308.1666
18.8 | [8 empty] | 2055.1058 | 2169.352 | 2485.2089 | 3332.4444
18.9 | [8 empty] | 2070.0529 | 2179.176 | 2505.6045 | 3356.7222
19 | [8 empty] | 2085 | 2189 | 2526 | 3381